## SGNet-Rqmts-Consumption-steps
The following are steps of making selections/decisions and specifying variables or selecting values from ranges that must be made to correctly consume the SG Network TF Requirements. Refer to the SG Network TF SRS for more details.
General Steps - Regardless of deployment analysis intent
1)Select the Deployment Profile, including endpoints, Use Cases, payload requirement sets to be used to extract the requirements from the SG Network TF Requirements ref "Deployment-Profiles" table/tab
a) Select the Deployment Profile – to be used to extract the requirements from the SG Network TF Requirements ref "Deployment-Profiles" table/tab
| selections /decisions made | ARHEMCdIW (with REPs, with HAN via ESI-InMtr, CIS-Utl direct to AMI Head-End, AMI Head-End-Inter-ExtranetGW-WAN-DAP) and DCSAfF (Centralized Apps & statusing, D-SCADA app to Fdr-Line-Device&substation,AMI Head-End for comm device mgmt, SCADA-Wan-FAN gateway-fld- FDRDevice)
b) Select the endpoints and other qualifications/conditions:
| selections /decisions made | i) Utility provides the wires connection to the Meter and transports any REP HAN traffic to the Customer HAN Devices via the Utility AMI Network and ESI in the electric meter for the REPs.
ii) Electric, Gas, Water meters in play with comm directly from AMI Network not via any HAN comm to the Gas & Water
iii) All HAN devices maybe a participant in appropriate REP programs
iv) The DAC in the substation is required for both Distr Customer Storage uses cases
v) the DAP and the FAN gateway - field actors may be considered one and the same
c) Determine what specific use-cases and payload requirement sets (ref parent rows in the Requirements Table), to model appropriate to the Deployment Profile (as restricted by the deployment profile from step 1a & 1b and use case dependencies identified in the SG Network TF SRS)
| selections /decisions made | i) Use Cases in Play: Cust. Info / Msgn'ng; Dispatch Distr. Cust. Storage; DR-DLC; DSDR - Centralized Control; FCIR - DMS; Field DA Maint - Centralized Control; Firmware / Program Update; Islanded Distr. Cust. Storage; Meter Events; Meter Reading; ORM; PHEV; Premise Network Admin; PrePay; Price; Service Switch; Volt/VAR - Centralized Control ii) Only the actors illustrated above are in play with these further restrictions: LMS - Utl in use for the Islanded Distr Cust. Storage, PHEV, Service Switch use cases and LMS - REPi in use for the DR-DLC and Price use cases
2) Identify which Requirement (Table or Database) payload requirement sets (parent rows and selected comm-paths) are in play based on selections and restrictions from step 1 above.
a) Flag the Deployment Profile' parent rows – Using the spreadsheet approach, create a copy (wip), of the full Requirement Table and append 1 column "Deployment Profile Use Case Payload Parents flag" to the "Reqmts-Combined" tab. Filter for parent rows and iterate through filtering for each in-scope use case, and place a flag entry in this newly added column.
b) Flag the Deployment Profile' child (or parents with no children) rows – use the wip Requirement Table (from step 2a), remove the parent row filter. Insert a working tab that contains a list of the interfaces and dataflows labels from the Deployment Profile Reference diagram and a child flag column that is populated with e.g. "x". Append 1 column "Deployment Profile comm-paths/rqmts flag" and enter a function that results in flagging those requirement rows that are an exact match to the Deployment Profile Ref Diagram e.g. use spreadsheet VLOOKUP function to flag the rows that match the interfaces & dataflows listed in that new tab.
c) Optionally Identify the child's parent Rqmt Ref (used for back reference and audit purposes) – use the wip Requirement Table (from step 2b), in a new tab or append columns to the tab added in 2b. Create a query in the Requirements Database that lists the child to parent Rqmt Ref pairings and copy/paste - those results into the new tab. Append 1 column to the wip Requirement Table "Child's Parent Rqmt Ref" and enter a function that results in showing the parent Rqmt Ref for that requirement rows parent e.g. use spreadsheet VLOOKUP function to list the parent Rqmt Ref that match the pairings listed in that new tab. Note: release 5.1 of the Rqmts Database produces this child to parent pairing that is 95% correct (it's being corrected), but you will need to perform a validation check in the spreadsheet. The alternative to using this approach is to write a spreadsheet macro that accomplishes the same result.
d) Extract the Deployment Profile Requirements to a Separate Workspace – Using the spreadsheet approach, extract the requirement rows from the wip Requirements Table from steps 2b and/or 2c above by filtering on the parent rows and the flagged child rows that satify the Deployment Profile and use case, payloads, comm-paths and endpoints selected AND save the results in a Deployment Profile analysis spreadsheet to reduce the working size of the sreadsheet versus always working with the full SG Network Requirements Table. To this spreadsheet copy the Paylaods tab as it will be used in further steps. The alternative to this is to delete all of the contents of this wip spreadsheet as the results os steps 2a,b,c that are outside the scope of the Deployment Profile.
| Results | The spreadsheet resulting from step 2d is one that is used for Steps 3-5 below. Step 7 will further reduce this Deployment Profile requirements rows down to just those specific to the PAP02 for a specific interface/dataflow(s) for processing and input into the wireless model.
3) Select one value for the documented non-functional metrics where ranges or unspecified parms (variables) are identified in Requirements tab, specific to your business requirements. Optionally, modify the other fixed/specified metrics to your business requirements.
a) How Often - the range value selection and declaring unspecified parms (variables) for this column is addressed in step 4c
b) Business App Payload Latency - use the wip Requirement Table (from step 2), append 1 column to the Requirements tab for "App Payload Latency (sec)", copy/modify just the numeric value from the contents of the existing column M latency and enter a numberic value in seconds for those that were documented as a range.
c) App Payload Size - use the wip Requirement Table (from step 3a), append 1 column to the Requirements tab for "App Payload Size (bytes)", copy/modify just the numeric value from the contents of the existing column N payload size and enter a numeric value in bytes for those that were documented as a range.
d) Daily Clock Period Factor for Specific Hour - use the wip Requirement Table (from step 3b), append 1 column to the Requirements tab for a multiplication factor to translate the primary period of a day down to a specific hour of the day. Note: if the intent is to deal with the whole 24 hr day and not focus on any particular hour, then enter "1" for the cells in this column.
| selections /decisions made | focus is on the 5pm hour: If the requirement rows Daily Clock Periods of Primary Occurrence is outside the hour of study, then enter a zero "0", otherwise enter the calculation (1 / (number of hours in daily primary clock periods)) for that requirement row.
4) Scale the non-functional app payload metrics in the Requirements tab specific to your deployment characteristics
a) Mutiple actor payloads multiplier for shared child row data flows /interfaces - several of the child row From-To actor pairs for 1 to many or many to 1 actor payload requirement sets, need to account for for those multiple flows as driven by the Data Flow Ref pseudo code. Use the wip Requirement Table (from step 3), append 1 column to the Requirements tab for "Rqmt Row Multiple Actor multiplier - max". If there is ony one payload being moved between the From-To actor pairs, enter "1", otherwise determine the maximum number of payloads per the stated From-To pairing and enter that value.
| selections /decisions made | e.g. for Data Flow Ref PNA-351 ESI - In Meter shall be able to process & forward HAN device join request acknowledgements to DAPjm. Maximum Rqmt row multiple actor multiplier = 6
b) How Often Actor Quantity conditional/qualified & root actor names - use the wip Requirement Table (from step 4a), append 2 columns to the Requirements tab for the" How Often Actor Quantity Qualifier/Conditional" AND the "Root Actor". Parse that row's How Often content (including the actor whose quanity drives how many payloads are in play and append that actor name/abbreviation (ref the Requirements Table "HowOften-abbrev-xref" tab) with the other specific payload occurrence conditions excluding the numeric How Often frequency metrics), and enter that composite actor label. Note: the selection of the root actor for intermediary actors is driven by the payload requirements set originating source actor and in some instances that actor may be a generic name such as HAN Device(s). In these conditions, use of the general root actor name is acceptable provided that the "Rqmt Row multi Actor multiplier - max" value is also entered. for that requirement row and accounting for those potential multiple payload flows.
Once all the How Often Actor quantity qualifiers and root names are entered, create a pivot/datapilot of those columns with row type as the column and store the unique values in a new tab (e.g. "3-Actor-Qtys"), to the spreadsheet that will be used in a step 4d. Group the unique conditional/qualified & root actors that make logical sense e.g. all entries associated to the different endpoints or program HAN device payloads. Optionally include additional input parameters e.g. % of a specific endpoint under specific conditions that gets applied to the total (or sub-category) of the specific root actor, that is to be used as the conditional/qualified actor quantity in other spreadsheet calculations. Populate the specific root actor' quantity into the appropriate cells and set the formulas as needed for scaling of the root actor quantities to the specifics of the qualified/conditional actors (excluding the "Rqmt Row multi Actor multiplier", which is handled separately).
Optionally, the default set of Model-Area endpoint Actor quantities (from SG-Networ-PAP02 modeling tool tabs "1-USA-states" and "2-Model-area" can be linked into the tab created in this step (e.g. "3-Actor-Qtys") and modified as per your deployment characteristics to parse out the Conditional/Qualified Actor quantities.
| selections /decisions made | e.g. for Data Flow Ref PNA-351, the qualified/conditional actor name is "ESIInMtr-with-HANdevice-REPi-join" and the root actor name is "ESIInMtr"
c) Payload Frequency metric per unit of time per How Often conditional/qualified Actor - use the wip Requirement Table (from step 4b), append 1 column to the Requirements tab for "Payload frequency metric per unit of time per qualified/conditional actor", a multiplication factor, that when multiplied by the qualified/conditional actor quantities, results in the number of the application payloads being transported over the data flow/interface for that specific From-To requirement row per unit of time. This multiplication factor also includes: i) making "How Often" range value selections and declaring unspecified parms (variables); ii) the Daily Clock Period Factor for Specific Hour factor; iii) Multiple actor payloads multiplier for shared child row data flows /interfaces factor.
| selections /decisions made | for Data Flow Ref PNA-351, the calculation for a time period of hour at 5pm would be [(1/365) * (Daily Clock Period Factor for Specific Hour factor) * (Multiple actor payloads multiplier)]
d) Conditional/Qualified Actor Quantities - use the wip Requirement Table (from step-answer 5c), append 1 column to the "Reqmts-Combined" tab for the Conditional/Qualified Actor Quantities. link the specific child row's Conditional/Qualified Actor Quantities cell to the same Conditional/Qualified Actor Quantity cell in the tab from the result of step 5b.
| selections /decisions made | for Data Flow Ref PNA-351, ESIInMtr-with-HANdevice-REPi-join actor quantiy is 206,400
Additional Steps - for PAP02 Wireless Traffic Modeling
6) Select which application payload data flow (may include interfaces) are to be analyzed
| answer: e.g. | Focus on the payload traffic of the DAP/FAN gatway - field between FAN & AMI Network Endpoint Actors specific to the use case payloads per the Deployment Profile in (1) e.g. all of the following data flows and interfaces, not just a single interface like MeA.
Interfaces: MeA, MgA, MwA, FA, FF, RGF, CBF,SF, STF, SWF, RCF, CGF, CSF
Dataflows: 1D, 1Dg, 1Dw, 5Ba, 6Me, 6Mg, 6Mw, 6FD, 4DFT, 4DRG, 4DCB, 4DS, 4DST, 4DSW, 4DRC, 4DCG, 4DCS, 4FRG, 4FCB, 4DS, 4FST, 4FSW, 4FRC, 4FCG, 4FCS, 4FFGa, 6FRG, 6FCB, 6FS, 6FST, 6FSW, 6FRC, 6FCG, 6FCS, 6FFGa
Using the spreadsheet approach, use the Requirement Table (from step 5), insert a working tab that contains a list of the interfaces and dataflows labels from the answers earlier in this step and a rqmt flag column that is populated with e.g. "x". Append 1 column to the "Reqmts-Combined" tab "PAP02 wireless modeling rqmt flag" and enter a function that results in flagging those requirement rows that are an exact match to the interfaces and dataflows listed in the inserted working tab e.g. use spreadsheet VLOOKUP function to flag the rows that match the interfaces & dataflows listed in that new tab. Filter the resultant modified "Reqmts-Combined" tab for non-blank "PAP02 wireless modeling rqmt flag" entries.
work in progress below this row
7) For Wireless traffic modeling needs, determine and specify the wireless "Uplink" and "Downlink" designation for the requirement rows
| answer: e.g. | Using the spreadsheet approach, use the Requirement Table (from step 6), append 1 column to the "Reqmts-Combined" tab for "Uplink or Downlink" value entries for each requirement row. Enter in that Uplink or Downlink flag e.g. "up" or "down" based on your assessment needs. For From-To payloads that are from one endpoint to another endpoint across a network cloud, make a copy of the child row and code one as the downlink and the other as uplink. This is to allow for traffic assessment of those technologies where endpoints must communicate to another endpoint via a DAP (basestation) versus peer-to-peer.
for traffic from DAP to endpoint flag as Downlink; for payloads from endpoint to DAP flag as Uplink
8) Create the Payload Frequency metric per unit of time per How Often conditional/qualified Actor for the payload Baseload and Highload conditions.
| answer: e.g. | Using the spreadsheet approach, the wip Requirement Table (from step 8), append 2 columns to the "Reqmts-Combined" tab for baseload and highload Payload Frequency metric per unit of time per How Often conditional/qualified Actor, for those rows identified in step 7. using the calculation described in step 5c
| answer: e.g. | Using the spreadsheet approach, the wip Requirement Table (from step 5), append 2 column to the "Reqmts-Combined" tab for baseload and highload flags for those payload requirement sets identified in step 2, using the baseload/highload designations in that SG Network has recently included in the Requirements Table "Payloads" tab and modify those as specific to your deployment profile. Note: if a use case payload requirement set is not abpplicable to the baseload or highload category the cell entries must be null.
10) Add columns to deal with Payload Packet size and latency versus Application Payloads
| answer: e.g. | Using the spreadsheet approach, the wip Requirement Table (from step 9), append 3 columns to the "Reqmts-Combined" tab for number of packets per app payload and packet latency. Specify a variable for packet size in bytes. i) in the rows' Number of packets cell, enter the roundup the results of the calculation (payload size bytes) / (packet size bytes) ii) in the rows' packet latency (sec) cell enter the results of the calculation (payload latency) / (number of packets)
11) For the combinations of the density categories, baseload and highload, and conditional/quality actor quantities, calculate the requirement metrics for that requirement row as needed for assembly as the SG Network Inputs to the PAP02 Wireless Modeling Tool
| answer: e.g. | need to add in the details of the calulations for the density category columns
12) Assemble the SG Network Inputs parameters for the PAP02 Wireless Modeling Tool
| answer: e.g. | Using the spreadsheet approach, the wip Requirement Table (from step 11), create the tab "5-SGNet-summarized-inputs" of SG Network Requirements inputs (metrics) as calculated and extracted from the "4-SG-Net-Rqmts-DAP-endpts" tab
13) Run the PAP02 Wireless Modeling Tool using the "5-SGNet-summarized-inputs" tab metrics. Capture the outputs of each required run the the modeling tool and store the results in the "8-Sum-Outputs" tab
ex cell calcs | Actor qty qualifiers | MID(K287,FIND("¦",K287)+2,(FIND("¦",K287,FIND("¦",K287)+1)-FIND("¦",K287)-7))

## 1-USA-states
Point Density Area Category Characteristics
| Densities |  |  | USA-States (only)
Density Area Category | Population1 per sq-mi | House-Units2 per sq-mi | House-unit cluster area3 (sq-mi) | % of Population | % of House-Units | % of "Land" Area | % of "Land" Area with hills/valley RF issues | % of "Land" Area with folliage RF issues | % of "Land" Area with RF noise floor issues | Modeling Concerns | data source
dense urban0,4 | median 18,005, 1563 - 229,713 | ≥ 4,000 | 180 places, median 1.00, range 0.02 - 303 | 11% | 11.51% | 0.05082% | tbd | tbd | tbd | High density of high rise buildings (office + residential), basement-located endpoints, etc | 2000 census tract data "ustracts2k.zip" from Census Bureau Gazetteer
urban0,5 | median 4646, 452 - 155,931 | ≥1000 - <4000 | 3,711 places median 2.12, range 0.01 - 579 | 34.68% | 34.31% | 0.6322% | tbd | tbd | tbd | Combination of commercial, industrial and residential. Varied building heights | 2000 census tract data "ustracts2k.zip" from Census Bureau Gazetteer
suburban0,6 | median 1071, 24 - 26,174 | ≥100 - <1000 | 17,755 places, median 1.47, range 0.02 - 757 | 30.69% | 29.77% | 3.248% | tbd | tbd | tbd | Comination of mostly residential (1-3 story) with some commercial (1-4 story) with areas terrain & foliage concerns | 2000 census tract data "ustracts2k.zip" from Census Bureau Gazetteer
rural7 | median 47.7, 0.7 - 466 | ≥10 - <100 | 3,033 places, median 3.12, range 0.04 - 400 | 17% | 17.6% | 22.71% | tbd | tbd | tbd | Foliage, rugged terrain, HU far apart plus some towns, long backhaul | 2000 census tract data "ustracts2k.zip" from Census Bureau Gazetteer, plus land area > 25 sq mi
low density rural7 | median 10.7, 0.002 - 108 | < 10 | 440 places, median 21.04, range 0.13 - 2,874 | 4.186% | 4.655% | 72.27% | tbd | tbd | tbd | Foliage, rugged terrain, HU far apart plus small communities or isolated towns, long backhaul. | 2000 census tract data "ustracts2k.zip" from Census Bureau Gazetteer, plus land area >= 50 sq mi
exclusions-rural |  |  |  | 2.449% | 2.155% | 1.087% |  |  |  | to be parsed into other areas. | to be parsed into other areas.
USA-State Totals (count or sq-mi) |  |  |  | 285133064 | 117322588 | 3535067 | tbd | tbd | tbd |  | 2000 census tract US-states data
Notes:
0) based on the census tract densities, not necessarily a census place's suburban, urban, dense urban zones
1) based on the census tracts with the specific category's house-units density criteria
2) based on a census tract's hous-units-qty / land sq-miles
3) based on census place land area ("places2k.zip" from Census Bureau Gazetteer), that satisfies the house-unit density criteria
4) commercial, residential zones
5) commercial, industrial, residential zones
6) residential, commercial, industrial zones
7) places, residential, commercial, industrial
work-in-progress
manual entry

## 2-model-area
Point Density Area Category Characteristics
| Density |  | USA-States - Model Area
Density Area Category | House-Units2 per sq-mi | House-unit cluster area3 (sq-mi) | % of Population | % of House-Units | % of "Land" Area | % of "Land" Area with hills/valley RF issues | % of "Land" Area with foliage RF issues | % of "Land" Area with noise floor RF issues | house-unit qty | comm'rcl & indust unit qty | electr mtrs - resdnt qty | electr mtrs C&I qty | electr mtrs qty | gas mtrs resdnt qty | gas mtrs C&I qty | gas mtrs qty | water mtrs resdnt qty | water mtrs C&I qty | water mtrs qty | Distr Substa | Distr Circuits | Distr Feeder Cap Bank | Distr Cust Gen | Distr Feeder Cust Strg | Distr Feeder Field Sensor | Distr Feeder Recloser | Distr Feeder Sectionalizer | Distr Feeder Switch | Distr Feeder Volt Regs | Total Potential end-points
dense urban0,4 | ≥ 4,000 | 4 places, median 1.00, range 0.02 - 303 | 11% | 11.51% | 0.05082% | tbd | tbd | tbd | 270000 | 47600 | 135000 | 71400 | 206400 | 135000 | 45200 | 180200 | 81000 | 45200 | 126200 | 18.0413 | 216.496 | [8 empty] | 512800
urban0,5 | ≥1000 - <4000 | 74 places median 2.12, range 0.01 - 579 | 34.68% | 34.31% | 0.6322% | tbd | tbd | tbd | 805000 | 142100 | 402500 | 213200 | 615700 | 402500 | 142100 | 544600 | 241500 | 142100 | 383600 | 56.1115 | 448.8923 | 897.7846 |  |  | 1122.2307 | 673.3384 |  | 448.8923 | 168.3346 | 1547210.5807
suburban0,6 | ≥100 - <1000 | 355 places, median 1.47, range 0.02 - 757 | 30.69% | 29.77% | 3.248% | tbd | tbd | tbd | 698000 | 123200 | 698000 | 184800 | 882800 | 593300 | 117000 | 710300 | 663100 | 246400 | 909500 | 102.4969 | 614.9811 | 2459.9246 |  | 49198.4911 | 3074.9057 | 1844.9434 |  | 1229.9623 | 461.2359 | 2560869.4628
rural7 | ≥10 - <100 | 60 places, median 3.12, range 0.04 - 400 | 17% | 17.6% | 22.71% | tbd | tbd | tbd | 413000 | 72900 | 413000 | 72900 | 485900 | 206500 | 69300 | 275800 | 206500 | 72900 | 279400 | 131.6528 | 263.3056 | 1053.2224 |  |  | 1316.5279 | 789.9168 |  | 526.6112 | 197.4792 | 1044983.7574
low density rural7 | < 10 | 9 places, median 21.04, range 0.13 - 2,874 | 4.186% | 4.655% | 72.27% | tbd | tbd | tbd | 109000 | 19200 | 98100 | 9600 | 107700 | 32700 | 18200 | 50900 | 21800 | 3800 | 25600 | 91.6247 | 183.2493 | 732.9974 |  |  | 916.2467 | 549.748 |  | 366.4987 | 137.437 | 186902.9278
Model Area Totals (count or sq-mi) |  |  | 5703000 | 2346000 | 71000 | #VALUE! | #VALUE! | #VALUE! | 2295000 | 405000 | 1746600 | 551900 | 2298500 | 1370000 | 391800 | 1761800 | 1213900 | 510400 | 1724300 | 399.9272 | 1726.9243 | 5143.9289 | 0 | 49198.4911 | 6429.9111 | 3857.9467 | 0 | 2571.9644 | 964.4867 | 9337457.1292
USA-States to Model-Area Reduction factor >> |  | 50 |  |  | ^ sg miles ^ | ^ sg miles ^ | ^ sg miles ^ | ^ sg miles ^
Notes:
0) based on the census tract densities, not necessarily a census place's suburban, urban, dense urban zones
1)
2) based on a census tract's hous-units-qty / land sq-miles
3) based on census place land area ("places2k.zip" from Census Bureau Gazetteer), that satisfies the house-unit density criteria
4) commercial, residential zones
5) commercial, industrial, residential zones
6) residential, commercial, industrial zones
7) places, residential, commercial, industrial | [11 empty] | link with Substation and circuit info
Legend: | work-in-progress / tbd
manual entry
Estimating factors:
residential accts | 85%
C&I accts | 15%
[10 empty] | points / x land sq miles >> |  |  | 10
Density Area Category | % of HU with electr primary mtrs | % of HU with gas primary mtrs | % of HU with water primary mtrs | avg qty electr mtrs per C&I | avg qty gas mtrs per C&I | avg qty water mtrs per C&I | Distr Substation Qty | Distr Feeder Circuits Qty | Distr Feeder Cap Bank | Distr Cust Gen | Distr Feeder Cust Strg | Distr Feeder Field Sensor | Distr Feeder Recloser | Distr Feeder Sectionalizer | Distr Feeder Switch | Distr Feeder Volt Regs
dense urban0,4 | 50% | 50% | 30% | 1.5 | 0.95 | 0.95 | 5 | 60 | outofscope | tbd | tbd | outofscope | outofscope | outofscope | outofscope | outofscope
urban0,5 | 50% | 50% | 30% | 1.5 | 1 | 1 | 1.25 | 10 | 20 | tbd | tbd | 25 | 15 | tbd | 10 | 3.75
suburban0,6 | 100% | 85% | 95% | 1.5 | 0.95 | 2 | 0.44444 | 2.6667 | 10.6667 | tbd | 213.3333 | 13.3333 | 8 | tbd | 5.3333 | 2
rural7 | 100% | 50% | 50% | 1 | 0.95 | 1 | 0.081633 | 0.16327 | 0.65306 | tbd | tbd | 0.81633 | 0.4898 | tbd | 0.32653 | 0.12245
low density rural7 | 90% | 30% | 20% | 0.5 | 0.95 | 0.2 | 0.017857 | 0.035714 | 0.14286 | tbd | tbd | 0.17857 | 0.10714 | tbd | 0.071429 | 0.026786
estimates
# reclosers / circuit |  | 3
# capbank Cntrl / circuit |  | 4
# EOL sensors / circuit |  | 5
# switches / circuit |  | 2
# volt regs / circuit |  | 0.75
|  | high den urban | urban | suburban | rural | low den rural
# dist circuits / dist substat |  | 12 | 8 | 6 | 2 | 2
land sqmi / asset sq mi |  | 1 | 1 | 1.5 | 3.5 | 8
circuit mi / circuit |  | 17 | 25 | 50 | 75 | 150
asset sq mi / circuit |  | 1 | 2.5 | 8 | 15 | 30
asset sq mi / distr substat |  | 2 | 8 | 15 | 35 | 70
#DCS / circuit suburban |  |  |  | 80
% of area(s) served by networked grids (out of scope), e.g.: a) no VVC; B)regulation gear in the substations; c) only field sensors and network protectors out on the networked circuits |  | 100% | 50%
security overhead factor

## 3-Actor-Qtys
Actor-Metric Labels |  |  |  | Model-Area Qty | [5 empty] | Actor qty qualifiers | Actor qty - root
Network Actors | Data Flow Ref | Actor qty - root | endpoint cnt flag | Totals | dense urban | urban | suburban | rural | low density rural | DAPjm | DAPjm
[10 empty] | ElectrC/IMtr | ElectrC/IMtr
seed for qty DAPs - #endpoints per DAPjm |  |  |  |  | 2500 | 3500 | 5000 | 2000 | 1000 | ElectrMtr | ElectrMtr
seed for qty DAPs - sq-miles per DAPjm |  |  |  |  | 1 | 1.5 | 3 | 3 | 3 | ElectrMtr-lost-power | ElectrMtr
seed qty of DAPjm (greater of #endpoints or sq-miles per DAP) |  | DAPjm |  | 70397 | 205 | 449 | 2306 | 16127 | 51310 | ElectrMtr-power-returned | ElectrMtr
% of Sub(x)FANgw updated by FieldTool |  |  |  |  | 1% | 0.5% | 0.5% | 0.5% | 1% | ElectrMtr-REPi-join | ElectrMtr
Sub(x)FANgw-update-from-FieldTool |  | Sub(x)FANgw | x | 3 | 0 | 0 | 1 | 1 | 1 | ElectrMtr-REPi-un-join | ElectrMtr
Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool |  | Sub(x)FANgw | x | 3 | 0 | 0 | 1 | 1 | 1 | ElectrMtr-update-from-FieldTool | ElectrMtr
[10 empty] | ElectrMtr-with-HANdevice-join | ElectrMtr
SAIFI (for a year) |  |  |  |  | 1 | 1 | 1.1 | 1.2 | 1.2 | ElectrMtr-with-HANdevice-joins-REPi | ElectrMtr
∑ of sustained outages in a year |  | ElectrMtr |  | 2505500 | 206400 | 615700 | 971080 | 583080 | 129240 | ElectrMtr-with-HANdevice-REPi-un-join | ElectrMtr
MAIFI (for a year) |  |  |  |  | 2 | 2 | 2.7 | 3 | 3 | ElectrMtr-with-HANdevice-un-join | ElectrMtr
∑ of momentary outages in a year |  | ElectrMtr |  | 5808560 | 412800 | 1231400 | 2383560 | 1457700 | 323100 | ElectrMtr-with-HANdevice-un-join | ESIInMtr
[10 empty] | ElectrResdIMtr | ElectrMtr
Electric Meter Items (quantities) | [9 empty] | ESIInMtr | ESIInMtr
ElectrResdIMtr |  | ElectrMtr |  | 1746600 | 135000 | 402500 | 698000 | 413000 | 98100 | ESIInMtr-connected-PHEV | PHEV
ElectrC/IMtr |  | ElectrC/IMtr |  | 551900 | 71400 | 213200 | 184800 | 72900 | 9600 | ESIInMtr-Mtr-with-HANdevice-join | ESIInMtr
ElectrMtr |  | ElectrMtr | x | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700 | ESIInMtr-Mtr-with-HANdevice-REPi-join | ESIInMtr
ElectrMtr-lost-power |  | ElectrMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700 | ESIInMtr-Mtr-with-HANdevice-REPi-un-join | ESIInMtr
ElectrMtr-power-returned |  | ElectrMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700 | ESIInMtr-Mtr-with-HANdevice-un-join | ESIInMtr
[10 empty] | ESIInMtr-PHEV | PHEV
avg # of ElectMtr associated to a specific feeder Distr Cust Storage |  |  |  |  | 0 | 0 | 5 | 0 | 0 | ESIInMtr-REPi-joined_ LMS - REPi vol-load-shed event | ESIInMtr
fdrDCS-ElectrMtr |  | ElectrMtr |  | 245992.4553 |  |  | 245992.4553 |  |  | ESIInMtr-REPi-joined-CPP-HANdevice_LMS - REPi CPP price data event | ESIInMtr
% of DCS-ElectrMtr-with-IPD-or-CustEMS |  |  |  |  | 0% | 0% | 10% | 0% | 0% | ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi direct load mgmt event | ESIInMtr
fdrDCS-ElectrMtr-with-IPD-or-CustEMS |  | ElectrMtr |  | 24599.2455 |  |  | 24599.2455 |  |  | ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi load Mgmt event | ESIInMtr
[10 empty] | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed broadcast request event | ESIInMtr
% of ElectrMtr that need updated by Field Tool per update event-period |  |  |  |  | 1% | 0.5% | 0.5% | 0.5% | 1% | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed multicast request event | ESIInMtr
ElectrMtr-update-from-FieldTool |  | ElectrMtr |  | 13063 | 2064 | 3078.5 | 4414 | 2429.5 | 1077 | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol-load-shed-event | ESIInMtr
[10 empty] | ESIInMtr-REPi-joined-RTP-HANdevice_LMS - REPi RTP price data event | ESIInMtr
% of ElectrMtr (Residential) that are PrePay |  |  |  |  | 5% | 5% | 5% | 5% | 5% | ESIInMtr-REPi-joined-TOU-HANdevice_LMS - REPi TOU price data event | ESIInMtr
PrePay-ElectrMtr |  | ElectrMtr |  | 87330 | 6750 | 20125 | 34900 | 20650 | 4905 | ESIInMtr-REPi-PrePay-Mtr-with-CustEMS | CustEMS
PrePay-ElectrMtr-on-demand-Mtr-Read |  | ElectrMtr |  | 87330 | 6750 | 20125 | 34900 | 20650 | 4905 | ESIInMtr-REPi-PrePay-Mtr-with-IPD | IPD
PrePay-ElectrMtr-SW-oper |  | ElectrMtr |  | 87330 | 6750 | 20125 | 34900 | 20650 | 4905 | ESIInMtr-with-HANdevice-REPi-join | ESIInMtr
Utl-PrePay-ElectrMtr |  | ElectrMtr |  | 87330 | 6750 | 20125 | 34900 | 20650 | 4905 | ESIInMtr-with-HANdevice-REPi-un-join | ESIInMtr
% of Utl Prepay ElectMtr joining or un-joining as baseload per year |  |  |  |  | 5% | 5% | 5% | 5% | 5% | fdrCB | fdrCB
Utl-PrePay-ElectrMtr |  | ElectrMtr |  | 4367 | 338 | 1006 | 1745 | 1033 | 245 | fdrCB-update-from-FieldTool | fdrCB
%of Utl ElectrMtr joining on initial Customer joins to PrePay as highload per year |  |  |  |  | 30% | 30% | 35% | 15% | 15% | fdrDCG | fdrDCG
Utl-PrePay-ElectrMtr |  | ElectrMtr |  | 24112 | 2025 | 6038 | 12215 | 3098 | 736 | fdrDCG-update-from-FieldTool | fdrDCG
[10 empty] | fdrDCS | fdrDCS
% of REPi HAN Device joining or un-joining as baseload per year |  |  |  | 0.05 | 5% | 5% | 5% | 5% | 5% | fdrDCS_detected-transformer-lose-of-power-event | fdrDCS
ElectrMtr-REPi-join | (PNA-309), (PNA-351) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385 | fdrDCS-detected-lose-of-power | fdrDCS
ElectrMtr-with-HANdevice-join | (PNA-196) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385 | fdrDCS-ElectrMtr | ElectrMtr
ElectrMtr-with-HANdevice-joins-REPi | (PNA-477) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385 | fdrDCS-ElectrMtr-with-IPD-or-CustEMS | ElectrMtr
ElectrMtr-REPi-un-join | (PNA-393), (PNA-435) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385 | fdrDCS-update-from-FieldTool | fdrDCS
ElectrMtr-with-HANdevice-un-join | (PNA-272) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385 | fdrFS | fdrFS
%of REPi HAN Device joining on initial Customer joins to REPi as highload per year |  |  |  | 0.28047 | 30% | 30% | 35% | 15% | 15% | fdrFS-update-from-FieldTool | fdrFS
ElectrMtr-REPi-join | (PNA-309), (PNA-351) | ElectrMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155 | fdrRC | fdrRC
ElectrMtr-with-HANdevice-join | (PNA-196) | ElectrMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155 | fdrRC-update-from-FieldTool | fdrRC
ElectrMtr-with-HANdevice-joins-REPi | (PNA-477) | ElectrMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155 | fdrST | fdrST
[10 empty] | fdrST-update-from-FieldTool | fdrST
% of Density Category ElectrMtr participating in ∑ REPi CPP |  |  |  |  | 10% | 10% | 10% | 5% | 5% | fdrSW | fdrSW
REPi-joined-CPP-ElectrMtr |  | ElectrMtr |  | 200170 | 20640 | 61570 | 88280 | 24295 | 5385 | fdrSW-update-from-FieldTool | fdrSW
REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data broadcast event |  | ElectrMtr |  | 1 | 1 | 1 | 1 | 1 | 1 | fdrVR | fdrVR
% of Density Category ElectrMtr participating in ∑ REPi CPP multicast event |  |  |  |  | 15% | 15% | 15% | 15% | 15% | fdrVR-update-from-FieldTool | fdrVR
REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data multicast request event |  | ElectrMtr |  | 30025.5 | 3096 | 9235.5 | 13242 | 3644.25 | 807.75 | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC | fdrRC
% of Density Category ElectrMtr participating in ∑ REPi CPP providing CPP acks |  |  |  |  | 50% | 50% | 50% | 50% | 50% | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST | fdrST
REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data event |  | ElectrMtr |  | 100085 | 10320 | 30785 | 44140 | 12147.5 | 2692.5 | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW | fdrSW
% of Density Category ElectrMtr participating in ∑ REPi RTP |  |  |  |  | 5% | 5% | 5% | 0% | 0% | FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrCrtBrk | fdrCrtBrk
REPi-joined-RTP-ElectrMtr |  | ElectrMtr |  | 85245 | 10320 | 30785 | 44140 | 0 | 0 | FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrRC | fdrRC
REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data broadcast event |  | ElectrMtr |  | 1 | 1 | 1 | 1 | 0 | 0 | FldFANgw(x)Sub(x)-fdrDCS | fdrDCS
% of Density Category ElectrMtr participating in ∑ REPi RTP multicast event |  |  |  |  | 15% | 15% | 15% | 15% | 15% | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | fdrRC
REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data multicast request event |  | ElectrMtr |  | 12786.75 | 1548 | 4617.75 | 6621 | 0 | 0 | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | fdrST
% of Density Category ElectrMtr participating in ∑ REPi RTP providing RTP acks |  |  |  |  | 90% | 90% | 80% | 0% | 0% | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | fdrSW
REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data event |  | ElectrMtr |  | 72306.5 | 9288 | 27706.5 | 35312 | 0 | 0 | GasC/IMtr | GasC/IMtr
% of Density Category ElectrMtr participating in ∑ REPi TOU |  |  |  |  | 100% | 100% | 100% | 100% | 100% | GasMtr | GasMtr
REPi-joined-TOU-ElectrMtr |  | ElectrMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700 | GasMtr-join | GasMtr
REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data broadcast event |  | ElectrMtr |  | 1 | 1 | 1 | 1 | 1 | 1 | GasMtr-REPi-join | GasMtr
% of Density Category ElectrMtr participating in ∑ REPi TOU multicast event |  |  |  |  | 15% | 15% | 15% | 15% | 15% | GasMtr-REPi-Mtr | GasMtr
REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data multicast request event |  |  |  | 344775 | 30960 | 92355 | 132420 | 72885 | 16155 | GasMtr-repI-Mtr-join | GasMtr
% of Density Category ElectrMtr participating in ∑ REPi TOU providing TOU acks |  |  |  |  | 50% | 50% | 50% | 50% | 50% | GasMtr-REPi-Mtr-un-join | GasMtr
REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data event |  | ElectrMtr |  | 1149250 | 103200 | 307850 | 441400 | 242950 | 53850 | GasMtr-REPi-un-join | GasMtr
% of Density Category ElectrMtr participating in ∑ REPi DRDLC |  |  |  |  | 15% | 15% | 20% | 10% | 10% | GasMtr-un-join | GasMtr
REPi-joined-DRDLC-ElectrMtr |  | ElectrMtr |  | 359235 | 30960 | 92355 | 176560 | 48590 | 10770 | GasMtr-update-from-FieldTool | GasMtr
REPi-joined-DRDLC-ElectrMtr_ LMS - REPi direct load mgmt event |  | ElectrMtr |  | 359235 | 30960 | 92355 | 176560 | 48590 | 10770 | GasResdntMtr | GasMtr
REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt broadcast request event |  | ElectrMtr |  | 1 | 1 | 1 | 1 | 1 | 1 | PrePay-ElectrMtr | ElectrMtr
% of Density Category ElectrMtr participating in ∑ REPi DRDLC multicast event |  |  |  |  | 15% | 15% | 15% | 15% | 15% | PrePay-ElectrMtr-on-demand-Mtr-Read | ElectrMtr
REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt multicast request event |  | ElectrMtr |  | 53885.25 | 4644 | 13853.25 | 26484 | 7288.5 | 1615.5 | PrePay-ElectrMtr-SW-oper | ElectrMtr
% of Density Category ElectrMtr participating in ∑ REPi DRDLC providing DRDLC acks |  |  |  |  | 50% | 50% | 50% | 50% | 50% | PrePay-GasMtr | GasMtr
REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load Mgmt event |  | ElectrMtr |  | 206560.125 | 17802 | 53104.125 | 101522 | 27939.25 | 6192.75 | PrePay-GasMtr-on-demand-Mtr-read | GasMtr
[10 empty] | PrePay-GasMtr-valve-oper | GasMtr
Gas Meter Items | [9 empty] | PrePay-WaterMtr | WaterMtr
GasResdntMtr |  | GasMtr |  | 1370000 | 135000 | 402500 | 593300 | 206500 | 32700 | PrePay-WaterMtr-on-demand-Mtr-Read | WaterMtr
GasC/IMtr |  | GasC/IMtr |  | 391800 | 45200 | 142100 | 117000 | 69300 | 18200 | REPi-joined-CPP-ElectrMtr | ElectrMtr
GasMtr |  | GasMtr | x | 1761800 | 180200 | 544600 | 710300 | 275800 | 50900 | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data broadcast event | ElectrMtr
[10 empty] | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data multicast request event | ElectrMtr
% of GasMtr that need updated by Field Tool per update event-period |  |  |  |  | 1% | 0.5% | 0.5% | 0.5% | 1% | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data event | ElectrMtr
GasMtr-update-from-FieldTool |  | GasMtr |  | 9964.5 | 1802 | 2723 | 3551.5 | 1379 | 509 | REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data broadcast event | ESIInMtr
[10 empty] | REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data multicast request event | ESIInMtr
% of ∑ REPi HAN Device joining or un-joining as baseload per year |  |  |  | 0.05 | 5% | 5% | 5% | 5% | 5% | REPi-joined-CPP-ESIInMtr-with-HANdevice | ESIInMtr
GasMtr-REPi-Mtr | (PNA-309) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ElectrMtr | ElectrMtr
GasMtr-repI-Mtr-join | (PNA-351) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi direct load mgmt event | ElectrMtr
GasMtr-join | (PNA-196) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt broadcast request event | ElectrMtr
GasMtr-REPi-join | (PNA-477) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load Mgmt event | ElectrMtr
GasMtr-REPi-un-join | (PNA-393), (PNA-519) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt multicast request event | ElectrMtr
GasMtr-REPi-Mtr-un-join | (PNA-435) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt broadcast request event | ESIInMtr
GasMtr-un-join | (PNA-272) | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt multicast request event | ESIInMtr
% of ∑ REPi HAN Device joining on initial Customer joins to REPi as highload per year |  |  |  | 0.29234 | 30% | 30% | 35% | 15% | 15% | REPi-joined-DRDLC-ESIInMtr-with-HANdevice | ESIInMtr
GasMtr-REPi-Mtr | (PNA-309) | GasMtr |  | 515050 | 54060 | 163380 | 248605 | 41370 | 7635 | REPi-joined-RTP-ElectrMtr | ElectrMtr
GasMtr-repI-Mtr-join | (PNA-351) | GasMtr |  | 515050 | 54060 | 163380 | 248605 | 41370 | 7635 | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data broadcast event | ElectrMtr
GasMtr-join | (PNA-196) | GasMtr |  | 515050 | 54060 | 163380 | 248605 | 41370 | 7635 | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data event | ElectrMtr
GasMtr-REPi-join | (PNA-477) | GasMtr |  | 515050 | 54060 | 163380 | 248605 | 41370 | 7635 | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data multicast request event | ElectrMtr
[10 empty] | REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data broadcast event | ESIInMtr
% of GasMtr that are PrePay |  |  |  |  | 5% | 5% | 5% | 5% | 5% | REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data multicast request event | ESIInMtr
PrePay-GasMtr |  | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-RTP-ESIInMtr-with-HANdevice | ESIInMtr
PrePay-GasMtr-on-demand-Mtr-read |  | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-TOU-ElectrMtr | ElectrMtr
PrePay-GasMtr-valve-oper |  | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data broadcast event | ElectrMtr
Utl-PrePay-GasMtr |  | GasMtr |  | 88090 | 9010 | 27230 | 35515 | 13790 | 2545 | REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data event | ElectrMtr
[10 empty] | REPi-joined-TOU-ElectrMtrLMS - REPi TOU price data multicast request event | ElectrMtr
Water Meter Items | [9 empty] | REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data broadcast event | ESIInMtr
WaterMtr |  | WaterMtr | x | 1724300 | 126200 | 383600 | 909500 | 279400 | 25600 | REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data multicast request event | ESIInMtr
[10 empty] | REPi-joined-TOU-ESIInMtr-with-HANdevice | ESIInMtr
% of WaterMtr that need updated by Field Tool per update event-period |  |  |  |  | 1% | 0.5% | 0.5% | 0.5% | 1% | Sub(x)DAC-Sub(x)FANgw-fdrDCS | fdrDCS
WaterMtr-update-from-FieldTool |  | WaterMtr |  | 9380.5 | 1262 | 1918 | 4547.5 | 1397 | 256 | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | fdrDCS
[10 empty] | Sub(x)FANgw-update-from-FieldTool | Sub(x)FANgw
% of WaterMtr that are PrePay |  |  |  |  | 5% | 5% | 5% | 5% | 5% | Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool | Sub(x)FANgw
PrePay-WaterMtr |  | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | Utl-PrePay-ElectrMtr | ElectrMtr
PrePay-WaterMtr-on-demand-Mtr-Read |  | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | Utl-PrePay-GasMtr | GasMtr
Utl-PrePay-WaterMtr |  | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | Utl-PrePay-WaterMtr | WaterMtr
[10 empty] | WaterMtr | WaterMtr
% of ∑ REPi HAN Device joining and un-joining as baseload per year |  |  |  | 0.05 | 5% | 5% | 5% | 5% | 5% | WaterMtr-REPi-join | WaterMtr
WaterMtr-REPi-join | (PNA-309), (PNA-351) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-REPi-un-join | WaterMtr
WaterMtr-with-HANdevice-join | (PNA-196) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-update-from-FieldTool | WaterMtr
WaterMtr-with-HANdevice-REPi-join | (PNA-477) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-with-HANdevice-join | WaterMtr
WaterMtr-REPi-un-join | (PNA-393), (PNA-435) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-with-HANdevice-REPi-join | WaterMtr
WaterMtr-with-HANdevice-REPi-un-join | (PNA-519) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-with-HANdevice-REPi-un-join | WaterMtr
WaterMtr-with-HANdevice-un-join | (PNA-272) | WaterMtr |  | 86215 | 6310 | 19180 | 45475 | 13970 | 1280 | WaterMtr-with-HANdevice-un-join | WaterMtr
%of ∑ REPi HAN Device joining on initial Customer joins to REPi as highload per year |  |  |  | 0.29984 | 30% | 30% | 35% | 15% | 15%
WaterMtr-REPi-join | (PNA-309), (PNA-351) | WaterMtr |  | 517015 | 37860 | 115080 | 318325 | 41910 | 3840
WaterMtr-with-HANdevice-join | (PNA-196) | WaterMtr |  | 517015 | 37860 | 115080 | 318325 | 41910 | 3840
WaterMtr-with-HANdevice-REPi-join | (PNA-477) | WaterMtr |  | 517015 | 37860 | 115080 | 318325 | 41910 | 3840
Feeder Device Items
fdrCB |  | fdrCB | x | 5143.9289 |  | 897.7846 | 2459.9246 | 1053.2224 | 732.9974
fdrDCG |  | fdrDCG | x
fdrDCS |  | fdrDCS | x | 49198.4911 |  |  | 49198.4911
fdrDCS-detected-lose-of-power |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
fdrDCS_detected-transformer-lose-of-power-event |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
FldFANgw(x)Sub(x)-fdrDCS |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
Sub(x)DAC-Sub(x)FANgw-fdrDCS |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
fdrFS |  | fdrFS | x | 6429.9111 |  | 1122.2307 | 3074.9057 | 1316.5279 | 916.2467
fdrRC |  | fdrRC | x | 3857.9467 |  | 673.3384 | 1844.9434 | 789.9168 | 549.748
fdrST |  | fdrST
fdrSW |  | fdrSW | x | 2571.9644 |  | 448.8923 | 1229.9623 | 526.6112 | 366.4987
fdrVR |  | fdrVR | x | 964.4867 |  | 168.3346 | 461.2359 | 197.4792 | 137.437
fdrCrtBrk |  | fdrCrtBrk |  | 1726.9243 | 216.496 | 448.8923 | 614.9811 | 263.3056 | 183.2493
% of Circuits in FCIR scenarios | [5 empty] | 50% | 50% | 5% | 0%
% of lockout signals from feeder circuit breakers | [5 empty] | 30% | 20% | 30% | 30%
FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrCrtBrk |  | fdrCrtBrk |  | 132 |  | 67 | 61 | 4 | 0
FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrRC |  | fdrRC |  | 1002 |  | 236 | 738 | 28 | 0
% of reconfig ops by feeder reclosers | [5 empty] | 50% | 50% | 50% | 50%
FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC |  | fdrRC |  | 649 |  | 168 | 461 | 20 | 0
FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST |  | fdrST
FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW |  | fdrSW |  | 432 |  | 112 | 307 | 13 | 0
% of isolate ops by feeder reclosers | [5 empty] | 30% | 30% | 30% | 30%
FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC |  | fdrRC |  | 390 |  | 101 | 277 | 12 | 0
FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST |  | fdrST
FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW |  | fdrSW |  | 605 |  | 157 | 430 | 18 | 0
fdrCB-update-from-FieldTool |  | fdrCB |  | 5143.9289 |  | 897.7846 | 2459.9246 | 1053.2224 | 732.9974
fdrDCG-update-from-FieldTool |  | fdrDCG
fdrDCS-update-from-FieldTool |  | fdrDCS |  | 49198.4911 |  |  | 49198.4911
fdrFS-update-from-FieldTool |  | fdrFS |  | 6429.9111 |  | 1122.2307 | 3074.9057 | 1316.5279 | 916.2467
fdrRC-update-from-FieldTool |  | fdrRC |  | 3857.9467 |  | 673.3384 | 1844.9434 | 789.9168 | 549.748
fdrST-update-from-FieldTool |  | fdrST
fdrSW-update-from-FieldTool |  | fdrSW |  | 2571.9644 |  | 448.8923 | 1229.9623 | 526.6112 | 366.4987
fdrVR-update-from-FieldTool |  | fdrVR |  | 964.4867 |  | 168.3346 | 461.2359 | 197.4792 | 137.437
HAN Device Items
ESIInMtr |  | ESIInMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700
% of ∑ REPi HAN Device joining or un-joining as baseload per year |  |  |  | 0.05 | 5% | 5% | 5% | 5% | 5%
ESIInMtr-Mtr-with-HANdevice-join | (PNA-196) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ESIInMtr-Mtr-with-HANdevice-REPi-join | (PNA-477) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ESIInMtr-with-HANdevice-REPi-join | (PNA-309), (PNA-351) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ElectrMtr-with-HANdevice-REPi-un-join | (PNA-519) | ElectrMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ESIInMtr-Mtr-with-HANdevice-un-join | (PNA-272) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ESIInMtr-Mtr-with-HANdevice-REPi-un-join | (PNA-519) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
ESIInMtr-with-HANdevice-REPi-un-join | (PNA-393), (PNA-435) | ESIInMtr |  | 114925 | 10320 | 30785 | 44140 | 24295 | 5385
% of ∑ REPi HAN Device joining on initial Customer joins to REPi as highload per year |  |  |  | 0.28047 | 30% | 30% | 35% | 15% | 15%
ESIInMtr-Mtr-with-HANdevice-join | (PNA-196) | ESIInMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155
ESIInMtr-Mtr-with-HANdevice-REPi-join | (PNA-477) | ESIInMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155
ESIInMtr-with-HANdevice-REPi-join | (PNA-309), (PNA-351) | ESIInMtr |  | 644650 | 61920 | 184710 | 308980 | 72885 | 16155
% of ∑ ESIInMtr-REPi-Prepay Customers with CustEMS |  |  |  |  | 15% | 15% | 5% | 0% | 0%
ESIInMtr-REPi-PrePay-Mtr-with-CustEMS |  | CustEMS |  | 19085.25 | 3310.5 | 9980.25 | 5794.5 | 0 | 0
% of ∑ ESIInMtr-REPi-Prepay Customers with IPD |  |  |  |  | 85% | 85% | 95% | 100% | 100%
ESIInMtr-REPi-PrePay-Mtr-with-IPD |  | IPD |  | 242549.75 | 18759.5 | 56554.75 | 110095.5 | 48410 | 8730
% of ElectrMtr with PHEV-EVSE |  |  |  |  | 2% | 2% | 10% | 0% | 0%
ESIInMtr-PHEV |  | PHEV |  | 104722 | 4128 | 12314 | 88280 | 0 | 0
ESIInMtr-connected-PHEV |  | PHEV |  | 104722 | 4128 | 12314 | 88280 | 0 | 0
ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol-load-shed-event |  | ESIInMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700
ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed broadcast request event |  | ESIInMtr |  | 1 | 1 | 1 | 1 | 1 | 1
% of Density Category ElectrMtr requested to participate in vol-load shed multicast event |  |  |  |  | 15% | 15% | 15% | 15% | 15%
ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed multicast request event |  | ESIInMtr |  | 344775 | 30960 | 92355 | 132420 | 72885 | 16155
% of Density Category ElectrMtr providing vol-load shed acks |  |  |  |  | 10% | 10% | 10% | 10% | 10%
ESIInMtr-REPi-joined_ LMS - REPi vol-load-shed event |  | ESIInMtr |  | 229850 | 20640 | 61570 | 88280 | 48590 | 10770
REPi-joined-CPP-ESIInMtr-with-HANdevice |  | ESIInMtr |  | 200170 | 20640 | 61570 | 88280 | 24295 | 5385
REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data broadcast event |  | ESIInMtr |  | 1 | 1 | 1 | 1 | 1 | 1
REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data multicast request event |  | ESIInMtr |  | 30025.5 | 3096 | 9235.5 | 13242 | 3644.25 | 807.75
ESIInMtr-REPi-joined-CPP-HANdevice_LMS - REPi CPP price data event |  | ESIInMtr |  | 100085 | 10320 | 30785 | 44140 | 12147.5 | 2692.5
REPi-joined-RTP-ESIInMtr-with-HANdevice |  | ESIInMtr |  | 85245 | 10320 | 30785 | 44140 | 0 | 0
REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data broadcast event |  | ESIInMtr |  | 1 | 1 | 1 | 1 | 0 | 0
REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data multicast request event |  | ESIInMtr |  | 12786.75 | 1548 | 4617.75 | 6621 | 0 | 0
ESIInMtr-REPi-joined-RTP-HANdevice_LMS - REPi RTP price data event |  | ESIInMtr |  | 72306.5 | 9288 | 27706.5 | 35312 | 0 | 0
REPi-joined-TOU-ESIInMtr-with-HANdevice |  | ESIInMtr |  | 2298500 | 206400 | 615700 | 882800 | 485900 | 107700
REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data broadcast event |  | ESIInMtr |  | 1 | 1 | 1 | 1 | 1 | 1
REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data multicast request event |  | ESIInMtr |  | 344775 | 30960 | 92355 | 132420 | 72885 | 16155
ESIInMtr-REPi-joined-TOU-HANdevice_LMS - REPi TOU price data event |  | ESIInMtr |  | 1149250 | 103200 | 307850 | 441400 | 242950 | 53850
REPi-joined-DRDLC-ESIInMtr-with-HANdevice |  | ESIInMtr |  | 359235 | 30960 | 92355 | 176560 | 48590 | 10770
ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi direct load mgmt event |  | ESIInMtr |  | 359235 | 30960 | 92355 | 176560 | 48590 | 10770
REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt broadcast request event |  | ESIInMtr |  | 1 | 1 | 1 | 1 | 1 | 1
REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt multicast request event |  | ESIInMtr |  | 53885.25 | 4644 | 13853.25 | 26484 | 7288.5 | 1615.5
ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi load Mgmt event |  | ESIInMtr |  | 206560.125 | 17802 | 53104.125 | 101522 | 27939.25 | 6192.75

## 4-SG-Net-Rqmts-DAP-endpts
[34 empty] | baseload | highload | uplink / downlink | HDenUrban Qualified Actor Qty |  | baseload | highload | uplink / downlink | HDenUrban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Urban Qualified Actor Qty |  | baseload | highload | uplink / downlink | Urban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Suburban Qualified Actor Qty |  | baseload | highload | uplink / downlink | Suburban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Rural Qualified Actor Qty |  | baseload | highload | uplink / downlink | Rural Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | LDenRural Qualified Actor Qty |  | baseload | highload | uplink / downlink | LDenRural Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | TotalArea Qualified Actor Qty |  | baseload | highload | uplink / downlink | TotalArea Qualified Actor Qty
[34 empty] | X |  | up | >0 |  |  | X | up | >0 | [6 empty] | X |  | up | >0 |  |  | X | up | >0 | [6 empty] | X |  | up | >0 |  |  | X | up | >0 | [6 empty] | X |  | up | >0 |  |  | X | up | >0 | [6 empty] | X |  | up | >0 |  |  | X | up | >0 | [6 empty] | X |  | up | >0 |  |  | X | up | >0
[34 empty] | baseload | highload | uplink / downlink | HDenUrban Qualified Actor Qty |  | baseload | highload | uplink / downlink | HDenUrban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Urban Qualified Actor Qty |  | baseload | highload | uplink / downlink | Urban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Suburban Qualified Actor Qty |  | baseload | highload | uplink / downlink | Suburban Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | Rural Qualified Actor Qty |  | baseload | highload | uplink / downlink | Rural Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | LDenRural Qualified Actor Qty |  | baseload | highload | uplink / downlink | LDenRural Qualified Actor Qty | [6 empty] | baseload | highload | uplink / downlink | TotalArea Qualified Actor Qty |  | baseload | highload | uplink / downlink | TotalArea Qualified Actor Qty
[34 empty] | X |  | down | >0 |  |  | X | down | >0 | [6 empty] | X |  | down | >0 |  |  | X | down | >0 | [6 empty] | X |  | down | >0 |  |  | X | down | >0 | [6 empty] | X |  | down | >0 |  |  | X | down | >0 | [6 empty] | X |  | down | >0 |  |  | X | down | >0 | [6 empty] | X |  | down | >0 |  |  | X | down | >0
[34 empty] | High Density Urban | [14 empty] | Urban | [14 empty] | Suburban | [14 empty] | Rural | [14 empty] | Low Density Rural | [14 empty] | Total Model Area
Original Source Requirements Table Release 5.1 | [37 empty] | Sq-mi >> | 36.0827 | [13 empty] | Sq-mi >> | 448.8923 | [13 empty] | Sq-mi >> | 2306.1793 | [13 empty] | Sq-mi >> | 16127.4674 | [13 empty] | Sq-mi >> | 51309.8159 | [13 empty] | Sq-mi >> | 51309.8159
Rqmt Ref | Row Type | Data Flow Ref - SG-Network TF Diag r5.1 | Data Flow from Actor | Data Flow to Actor | Use Case Ref | Requirements | Payload Name - Specific Data/Mesg | Payload Type | Daily Clock Periods of Primary Occurrence | How Often | Reliability | Latency Rqmts | App Payload Size - bytes | how Often Time Metric | Discuss flag | baseload | highload | uplink / downlink | PAP02 profile for modeling - parent row flag | PAP02 profile for modeling DAP to Endpoints + Field Tool | Child's - Parent Row Rqmt Ref | endpoint to endpoint comm payload flag | endpoint to endpoint payload latency link factor | daily clock period factor for 5-6pm hour (as needed) | Rqmt row multi Actor multiplier - max | Actor qty - root | Actor qty qualifiers | payload latency (sec) | packet latency (sec) | payload size bytes | # of packets | baseload frequency metric per sec during 5-6pm period per qualified Actor | high load frequency metric per sec during 5-6pm period per qualified Actor | HDenUrban Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc | Urban Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc | Suburban Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc | Rural Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc | LDenRural Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc | TotalArea Qualified Actor Qty | baseload payload rate / sec | highload payload rate / sec | baseload packet rate / sec | highload packet rate / sec | baseload MBps /sq-mi | highload MBps /sq-mi | baseload payload size bytes - partial calc | highload payload size bytes - partial calc | baseload packet size bytes - partial calc - variable packet size | highload packet size bytes - partial calc - variable packet size | baseload payload latency sec - partial calc | highload payload latency sec - partial calc | baseload packet latency sec - partial calc | highload packet latency sec - partial calc
DDCS-003 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward device status (voltage, real & reactive power, avail energy) request to Distr. Cust. Storage | distr_cust_storage_status_cmd | cmd | 24x7 | 288 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ day | > 99.5% | < 4 sec | 25 | day | N | X | X | up |  | x | DDCS-001 | D | 0.5 | 0.041667 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899
DDCS-003 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward device status (voltage, real & reactive power, avail energy) request to Distr. Cust. Storage | distr_cust_storage_status_cmd | cmd | 24x7 | 288 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ day | > 99.5% | < 4 sec | 25 | day | N | X | X | down |  | x | DDCS-001 | D | 0.5 | 0.041667 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899
DDCS-005 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to process & send device status response data to the FAN gateway - sub | distr_cust_storage_status_resp-data | resp-data | 24x7 | 288 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ day | > 99.5% | < 4 sec | 50 | day | N | X | X | up |  | x | DDCS-004 | D | 0.5 | 0.041667 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899
DDCS-005 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to process & send device status response data to the FAN gateway - sub | distr_cust_storage_status_resp-data | resp-data | 24x7 | 288 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ day | > 99.5% | < 4 sec | 50 | day | N | X | X | down |  | x | DDCS-004 | D | 0.5 | 0.041667 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 327.9899 | 327.9899 | 327.9899 | 327.9899
DDCS-021 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward specific energy discharge rate request to each in-scope Distr. Cust. Storage | distr_cust_storage_discharge_cmd | cmd | 5AM - 9AM or 3PM - 7PM | 2-6 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ dispatch-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | up |  | x | DDCS-019 | D | 0.5 | 0.25 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00027778 | 0.00027778 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 2.963e-07 | 2.963e-07 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 1.3317e-08 | 1.3317e-08 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325
DDCS-021 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward specific energy discharge rate request to each in-scope Distr. Cust. Storage | distr_cust_storage_discharge_cmd | cmd | 5AM - 9AM or 3PM - 7PM | 2-6 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ dispatch-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | down |  | x | DDCS-019 | D | 0.5 | 0.25 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00027778 | 0.00027778 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 2.963e-07 | 2.963e-07 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 1.3317e-08 | 1.3317e-08 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325
DDCS-023 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to send receipt of discharge rate request acknowledgement to FAN gateway - sub | distr_cust_storage_discharge_cmd_ack | ack | 5AM - 9AM or 3PM - 7PM | 2-6 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ dispatch-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | up |  | x | DDCS-022 | D | 0.5 | 0.25 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00027778 | 0.00027778 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 2.963e-07 | 2.963e-07 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 1.3317e-08 | 1.3317e-08 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325
DDCS-023 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to send receipt of discharge rate request acknowledgement to FAN gateway - sub | distr_cust_storage_discharge_cmd_ack | ack | 5AM - 9AM or 3PM - 7PM | 2-6 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ dispatch-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | down |  | x | DDCS-022 | D | 0.5 | 0.25 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00027778 | 0.00027778 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 2.963e-07 | 2.963e-07 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325 | [30 empty] | 49198.4911 | 13.6662 | 13.6662 | 13.6662 | 13.6662 | 1.3317e-08 | 1.3317e-08 | 683.3124 | 683.3124 | 683.3124 | 683.3124 | 27.3325 | 27.3325 | 27.3325 | 27.3325
DDCS-027 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward specific charge-rate request to Distr. Cust. Storage | distr_cust_storage_charge-rate_cmd | cmd | 10pm - 5am | 2-4 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ charge-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | up |  | x | DDCS-025 | D | 0.5 | 0.14286 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00015873 | 0.00015873 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 1.6931e-07 | 1.6931e-07 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 7.6099e-09 | 7.6099e-09 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186
DDCS-027 | c | 4ECS | FAN gateway - sub | Distr. Cust. Storage | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & forward specific charge-rate request to Distr. Cust. Storage | distr_cust_storage_charge-rate_cmd | cmd | 10pm - 5am | 2-4 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ charge-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | down |  | x | DDCS-025 | D | 0.5 | 0.14286 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00015873 | 0.00015873 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 1.6931e-07 | 1.6931e-07 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 7.6099e-09 | 7.6099e-09 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186
DDCS-029 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to send receipt of charge-rate request acknowledgement to FAN gateway - sub | distr_cust_storage_charge-rate_cmd_ack | ack | 10pm - 5am | 2-4 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ charge-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | up |  | x | DDCS-028 | D | 0.5 | 0.14286 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00015873 | 0.00015873 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 1.6931e-07 | 1.6931e-07 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 7.6099e-09 | 7.6099e-09 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186
DDCS-029 | c | 4ECS | Distr. Cust. Storage | FAN gateway - sub | Dispatch Distr. Cust. Storage | Distr. Cust. Storage shall be able to send receipt of charge-rate request acknowledgement to FAN gateway - sub | distr_cust_storage_charge-rate_cmd_ack | ack | 10pm - 5am | 2-4 per ¦ Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS per ¦ charge-period per day | > 99.5% | < 4 sec | 25 | day | N | X | X | down |  | x | DDCS-028 | D | 0.5 | 0.14286 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-Sub(x)FANgw-fdrDCS | 2 | 2 | 50 | 1 | 0.00015873 | 0.00015873 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 1.6931e-07 | 1.6931e-07 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186 | [30 empty] | 49198.4911 | 7.8093 | 7.8093 | 7.8093 | 7.8093 | 7.6099e-09 | 7.6099e-09 | 390.4642 | 390.4642 | 390.4642 | 390.4642 | 15.6186 | 15.6186 | 15.6186 | 15.6186
DDCS-x1 | c | 4FFGa | FAN gateway - sub | FAN gateway - field | Dispatch Distr. Cust. Storage | FAN gateway - sub shall be able to process & send Distr. Cust. Storage device status response data to FAN gateway - field | distr_cust_storage_status_resp-data | resp-data | 24x7 | 288 per ¦ FldFANgw(x)Sub(x)-fdrDCS per ¦ day | > 99.5% | < 2 sec | 50 | day | N | X | X | up |  | x | DDCS-008 | D | 0.5 | 0.041667 | 1 | fdrDCS | FldFANgw(x)Sub(x)-fdrDCS | 1 | 1 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 163.995 | 163.995 | 163.995 | 163.995 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 163.995 | 163.995 | 163.995 | 163.995
DDCS-x1 | c | 4FFGa | FAN gateway - sub | FAN gateway - field | Dispatch Distr. Cust. Storage | DAC - sub shall be able to process & send Distr. Cust. Storage device status response data to Distr. SCADA FEP | distr_cust_storage_status_resp-data | resp-data | 24x7 | 288 per ¦ Sub(x)DAC-Sub(x)FANgw-fdrDCS per ¦ day | > 99.5% | < 2 sec | 50 | day | N | X | X | up |  | x | DDCS-008 | D | 0.5 | 0.041667 | 1 | fdrDCS | Sub(x)DAC-Sub(x)FANgw-fdrDCS | 1 | 1 | 50 | 1 | 0.0033333 | 0.0033333 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 3.5556e-06 | 3.5556e-06 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 163.995 | 163.995 | 163.995 | 163.995 | [30 empty] | 49198.4911 | 163.995 | 163.995 | 163.995 | 163.995 | 1.5981e-07 | 1.5981e-07 | 8199.7485 | 8199.7485 | 8199.7485 | 8199.7485 | 163.995 | 163.995 | 163.995 | 163.995
DR-0544 | c | 1D | DAPjm | 2-Way Meter - Electr | DR-DLC | DAPjm shall be able to send Direct Load Management request to the 2-Way Meter - Electr | Load_mgm_reqst | cmd | 24x7 | 60 per 1000 per ¦ REPi-joined-DRDLC-ElectrMtr per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | DR-0535 |  |  | 0.041667 | 1 | ElectrMtr | REPi-joined-DRDLC-ElectrMtr | 5 | 5 | 100 | 1 |  | 6.9444e-07 | 30960 |  | 0.0215 |  | 0.0215 |  | 5.9585e-08 |  | 2.15 |  | 2.15 |  | 0.1075 |  | 0.1075 | 92355 |  | 0.064135 |  | 0.064135 |  | 1.4287e-08 |  | 6.4135 |  | 6.4135 |  | 0.32068 |  | 0.32068 | 176560 |  | 0.12261 |  | 0.12261 |  | 3.3981e-07 |  | 12.2611 |  | 12.2611 |  | 0.61306 |  | 0.61306 | 48590 |  | 0.033743 |  | 0.033743 |  | 2.0923e-10 |  | 3.3743 |  | 3.3743 |  | 0.16872 |  | 0.16872 | 10770 |  | 0.0074792 |  | 0.0074792 |  | 1.4576e-11 |  | 0.74792 |  | 0.74792 |  | 0.037396 |  | 0.037396 | 359235 |  | 0.24947 |  | 0.24947 |  | 4.862e-10 |  | 24.9469 |  | 24.9469 | 0 | 1.2473 | 0 | 1.2473
DR-0545 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Direct Load Management request to ESI - In Meter | Load_mgm_reqst | cmd | 24x7 | 60 per 1000 per ¦ REPi-joined-DRDLC-ESIInMtr-with-HANdevice per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | DR-0535 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-DRDLC-ESIInMtr-with-HANdevice | 5 | 5 | 100 | 1 |  | 4.1667e-06 | 30960 |  | 0.129 |  | 0.129 |  | 3.5751e-07 |  | 12.9 |  | 12.9 |  | 0.645 |  | 0.645 | 92355 |  | 0.38481 |  | 0.38481 |  | 8.5725e-08 |  | 38.4813 |  | 38.4813 |  | 1.9241 |  | 1.9241 | 176560 |  | 0.73567 |  | 0.73567 |  | 2.0388e-06 |  | 73.5667 |  | 73.5667 |  | 3.6783 |  | 3.6783 | 48590 |  | 0.20246 |  | 0.20246 |  | 1.2554e-09 |  | 20.2458 |  | 20.2458 |  | 1.0123 |  | 1.0123 | 10770 |  | 0.044875 |  | 0.044875 |  | 8.7459e-11 |  | 4.4875 |  | 4.4875 |  | 0.22437 |  | 0.22437 | 359235 |  | 1.4968 |  | 1.4968 |  | 2.9172e-09 |  | 149.6813 |  | 149.6813 | 0 | 7.4841 | 0 | 7.4841
DR-0578 | c | 1D | DAPjm | 2-Way Meter - Electr | DR-DLC | DAPjm shall be able to send Direct Load Management broadcast request to the 2-Way Meter - Electr | Load_mgm_reqst_brdcst | cmd | 24x7 | 1 per ¦ REPi-joined-DRDLC-ElectrMtr per ¦ LMS - REPi load mgmt broadcast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0569 |  |  | 0.041667 | 1 | ElectrMtr | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt broadcast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
DR-0579 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Direct Load Management broadcast request to ESI - In Meter | Load_mgm_reqst_brdcst | cmd | 24x7 | 1 per ¦ REPi-joined-DRDLC-ESIInMtr per ¦ LMS - REPi load mgmt broadcast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0569 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt broadcast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
DR-0612 | c | 1D | DAPjm | 2-Way Meter - Electr | DR-DLC | DAPjm shall be able to send Direct Load Management multicast request to the 2-Way Meter - Electr | Load_mgm_reqst_mltcst | cmd | 24x7 | 1 per ¦ REPi-joined-DRDLC-ElectrMtr per ¦ LMS - REPi load mgmt multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0603 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load mgmt multicast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 4644 |  | 0.05375 |  | 0.05375 |  | 1.4896e-07 |  | 5.375 |  | 5.375 |  | 0.26875 |  | 0.26875 | 13853.25 |  | 0.16034 |  | 0.16034 |  | 3.5719e-08 |  | 16.0339 |  | 16.0339 |  | 0.80169 |  | 0.80169 | 26484 |  | 0.30653 |  | 0.30653 |  | 8.4952e-07 |  | 30.6528 |  | 30.6528 |  | 1.5326 |  | 1.5326 | 7288.5 |  | 0.084358 |  | 0.084358 |  | 5.2307e-10 |  | 8.4358 |  | 8.4358 |  | 0.42179 |  | 0.42179 | 1615.5 |  | 0.018698 |  | 0.018698 |  | 3.6441e-11 |  | 1.8698 |  | 1.8698 |  | 0.09349 |  | 0.09349 | 53885.25 |  | 0.62367 |  | 0.62367 |  | 1.2155e-09 |  | 62.3672 |  | 62.3672 | 0 | 3.1184 | 0 | 3.1184
DR-0613 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Direct Load Management multicast request to ESI - In Meter | Load_mgm_reqst_mltcst | cmd | 24x7 | 1 per ¦ REPi-joined-DRDLC-ESIInMtr per ¦ LMS - REPi load mgmt multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0603 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-DRDLC-ESIInMtr_ LMS - REPi load mgmt multicast request event | 5 | 5 | 100 | 1 |  | 6.9444e-05 | 4644 |  | 0.3225 |  | 0.3225 |  | 8.9378e-07 |  | 32.25 |  | 32.25 |  | 1.6125 |  | 1.6125 | 13853.25 |  | 0.96203 |  | 0.96203 |  | 2.1431e-07 |  | 96.2031 |  | 96.2031 |  | 4.8102 |  | 4.8102 | 26484 |  | 1.8392 |  | 1.8392 |  | 5.0971e-06 |  | 183.9167 |  | 183.9167 |  | 9.1958 |  | 9.1958 | 7288.5 |  | 0.50615 |  | 0.50615 |  | 3.1384e-09 |  | 50.6146 |  | 50.6146 |  | 2.5307 |  | 2.5307 | 1615.5 |  | 0.11219 |  | 0.11219 |  | 2.1865e-10 |  | 11.2188 |  | 11.2188 |  | 0.56094 |  | 0.56094 | 53885.25 |  | 3.742 |  | 3.742 |  | 7.293e-09 |  | 374.2031 |  | 374.2031 | 0 | 18.7102 | 0 | 18.7102
DR-0638 | c | 1D | 2-Way Meter - Electr | DAPjm | DR-DLC | 2-Way Meter - Electr shall be able to send Direct Load Management request acknowlegements to the DAPjm | Load_mgm_req_ack | ack | 24x7 | x per 1000 per ¦ REPi-joined-DRDLC-ElectrMtr per ¦ LMS - REPi load Mgmt event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | DR-0637 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi load Mgmt event | 5 | 5 | 25 | 1 |  | 1.1574e-05 | 17802 |  | 0.20604 |  | 0.20604 |  | 1.4276e-07 |  | 5.151 |  | 5.151 |  | 1.0302 |  | 1.0302 | 53104.125 |  | 0.61463 |  | 0.61463 |  | 3.423e-08 |  | 15.3658 |  | 15.3658 |  | 3.0732 |  | 3.0732 | 101522 |  | 1.175 |  | 1.175 |  | 8.1412e-07 |  | 29.3756 |  | 29.3756 |  | 5.8751 |  | 5.8751 | 27939.25 |  | 0.32337 |  | 0.32337 |  | 5.0127e-10 |  | 8.0843 |  | 8.0843 |  | 1.6169 |  | 1.6169 | 6192.75 |  | 0.071675 |  | 0.071675 |  | 3.4923e-11 |  | 1.7919 |  | 1.7919 |  | 0.35838 |  | 0.35838 | 206560.125 |  | 2.3907 |  | 2.3907 |  | 1.1649e-09 |  | 59.7686 |  | 59.7686 | 0 | 11.9537 | 0 | 11.9537
DR-0641 | c | 5Ba | ESI - In Meter | DAPjm | DR-DLC | ESI - In Meter shall be able to process & forward Direct Load Management request acknowledgements to DAPjm | Load_mgm_req_ack | ack | 24x7 | x per 1000 per ¦ ESIInMtr-REPi-joined-DRDLC-HANdevice per ¦ LMS - REPi load Mgmt event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | DR-0637 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi load Mgmt event | 5 | 5 | 25 | 1 |  | 6.9444e-05 | 17802 |  | 1.2363 |  | 1.2363 |  | 8.5654e-07 |  | 30.9062 |  | 30.9062 |  | 6.1813 |  | 6.1813 | 53104.125 |  | 3.6878 |  | 3.6878 |  | 2.0538e-07 |  | 92.1947 |  | 92.1947 |  | 18.4389 |  | 18.4389 | 101522 |  | 7.0501 |  | 7.0501 |  | 4.8847e-06 |  | 176.2535 |  | 176.2535 |  | 35.2507 |  | 35.2507 | 27939.25 |  | 1.9402 |  | 1.9402 |  | 3.0076e-09 |  | 48.5056 |  | 48.5056 |  | 9.7011 |  | 9.7011 | 6192.75 |  | 0.43005 |  | 0.43005 |  | 2.0954e-10 |  | 10.7513 |  | 10.7513 |  | 2.1503 |  | 2.1503 | 206560.125 |  | 14.3445 |  | 14.3445 |  | 6.9891e-09 |  | 358.6113 |  | 358.6113 | 0 | 71.7223 | 0 | 71.7223
DR-0680 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Volunteer Load Shed request to ESI - In Meter | Vol_load_shed_reqst | cmd | 24x7 | 60 per 1000 per ¦ ESIInMtr-REPi-joined-HANdevice per ¦ LMS - REPi vol-load-shed-event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0671 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol-load-shed-event | 5 | 5 | 100 | 1 |  | 4.1667e-06 | 206400 |  | 0.86 |  | 0.86 |  | 2.3834e-06 |  | 86 |  | 86 |  | 4.3 |  | 4.3 | 615700 |  | 2.5654 |  | 2.5654 |  | 5.715e-07 |  | 256.5417 |  | 256.5417 |  | 12.8271 |  | 12.8271 | 882800 |  | 3.6783 |  | 3.6783 |  | 1.0194e-05 |  | 367.8333 |  | 367.8333 |  | 18.3917 |  | 18.3917 | 485900 |  | 2.0246 |  | 2.0246 |  | 1.2554e-08 |  | 202.4583 |  | 202.4583 |  | 10.1229 |  | 10.1229 | 107700 |  | 0.44875 |  | 0.44875 |  | 8.7459e-10 |  | 44.875 |  | 44.875 |  | 2.2437 |  | 2.2437 | 2298500 |  | 9.5771 |  | 9.5771 |  | 1.8665e-08 |  | 957.7083 |  | 957.7083 | 0 | 47.8854 | 0 | 47.8854
DR-0711 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Volunteer Load Shed broadcast request to ESI - In Meter | Vol_load_shed_reqst_brdcst | cmd | 24x7 | 1 per ¦ ESIInMtr-REPi-joined-HANdevice per ¦ LMS - REPi vol load shed broadcast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0702 |  |  | 0.041667 | 1 | ESIInMtr | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed broadcast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
DR-0742 | c | 5Ba | DAPjm | ESI - In Meter | DR-DLC | DAPjm shall be able to process & forward Volunteer Load Shed multicast request to ESI - In Meter | Vol_load_shed_reqst_mltcst | cmd | 24x7 | 1 per ¦ ESIInMtr-REPi-joined-HANdevice per ¦ LMS - REPi vol load shed multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | DR-0733 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-HANdevice_ LMS - REPi vol load shed multicast request event | 5 | 5 | 100 | 1 |  | 6.9444e-05 | 30960 |  | 2.15 |  | 2.15 |  | 5.9585e-06 |  | 215 |  | 215 |  | 10.75 |  | 10.75 | 92355 |  | 6.4135 |  | 6.4135 |  | 1.4287e-06 |  | 641.3542 |  | 641.3542 |  | 32.0677 |  | 32.0677 | 132420 |  | 9.1958 |  | 9.1958 |  | 2.5485e-05 |  | 919.5833 |  | 919.5833 |  | 45.9792 |  | 45.9792 | 72885 |  | 5.0615 |  | 5.0615 |  | 3.1384e-08 |  | 506.1458 |  | 506.1458 |  | 25.3073 |  | 25.3073 | 16155 |  | 1.1219 |  | 1.1219 |  | 2.1865e-09 |  | 112.1875 |  | 112.1875 |  | 5.6094 |  | 5.6094 | 344775 |  | 23.9427 |  | 23.9427 |  | 4.6663e-08 |  | 2394.2708 |  | 2394.2708 | 0 | 119.7135 | 0 | 119.7135
DR-0766 | c | 5Ba | ESI - In Meter | DAPjm | DR-DLC | ESI - In Meter shall be able to process & forward Volunteer Load Shed request acknowledgements to DAPjm | Vol_load_shed_req_ack | ack | 24x7 | y per 1000 per ¦ ESIInMtr-REPi-joined per ¦ LMS - REPi vol-load-shed event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | DR-0764 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined_ LMS - REPi vol-load-shed event | 5 | 5 | 25 | 1 |  | 6.9444e-05 | 20640 |  | 1.4333 |  | 1.4333 |  | 9.9309e-07 |  | 35.8333 |  | 35.8333 |  | 7.1667 |  | 7.1667 | 61570 |  | 4.2757 |  | 4.2757 |  | 2.3812e-07 |  | 106.8924 |  | 106.8924 |  | 21.3785 |  | 21.3785 | 88280 |  | 6.1306 |  | 6.1306 |  | 4.2476e-06 |  | 153.2639 |  | 153.2639 |  | 30.6528 |  | 30.6528 | 48590 |  | 3.3743 |  | 3.3743 |  | 5.2307e-09 |  | 84.3576 |  | 84.3576 |  | 16.8715 |  | 16.8715 | 10770 |  | 0.74792 |  | 0.74792 |  | 3.6441e-10 |  | 18.6979 |  | 18.6979 |  | 3.7396 |  | 3.7396 | 229850 |  | 15.9618 |  | 15.9618 |  | 7.7772e-09 |  | 399.0451 |  | 399.0451 | 0 | 79.809 | 0 | 79.809
DR-0796 | c | 1D | 2-Way Meter - Electr | DAPjm | DR-DLC | 2-Way Meter - Electr shall be able to send Direct Load Management request opt out message to DAPjm | Load_mgm_opt_out | cmd | 24x7 | 10 per 1000 per ¦ REPi-joined-DRDLC-ElectrMtr per ¦ LMS - REPi direct load mgmt event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | DR-0795 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-DRDLC-ElectrMtr_ LMS - REPi direct load mgmt event | 5 | 5 | 25 | 1 |  | 1.1574e-07 | 30960 |  | 0.0035833 |  | 0.0035833 |  | 2.4827e-09 |  | 0.089583 |  | 0.089583 |  | 0.017917 |  | 0.017917 | 92355 |  | 0.010689 |  | 0.010689 |  | 5.9531e-10 |  | 0.26723 |  | 0.26723 |  | 0.053446 |  | 0.053446 | 176560 |  | 0.020435 |  | 0.020435 |  | 1.4159e-08 |  | 0.51088 |  | 0.51088 |  | 0.10218 |  | 0.10218 | 48590 |  | 0.0056238 |  | 0.0056238 |  | 8.7178e-12 |  | 0.1406 |  | 0.1406 |  | 0.028119 |  | 0.028119 | 10770 |  | 0.0012465 |  | 0.0012465 |  | 6.0735e-13 |  | 0.031163 |  | 0.031163 |  | 0.0062326 |  | 0.0062326 | 359235 |  | 0.041578 |  | 0.041578 |  | 2.0258e-11 |  | 1.0395 |  | 1.0395 | 0 | 0.20789 | 0 | 0.20789
DR-0799 | c | 5Ba | ESI - In Meter | DAPjm | DR-DLC | ESI - In Meter shall be able to process & forward Direct Load Management request opt out message to DAPjm | Load_mgm_opt_out | cmd | 24x7 | 10 per 1000 per ¦ ESIInMtr-REPi-joined-DRDLC-HANdevice per ¦ LMS - REPi direct load mgmt event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | DR-0795 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-DRDLC-HANdevice_ LMS - REPi direct load mgmt event | 5 | 5 | 25 | 1 |  | 6.9444e-07 | 30960 |  | 0.0215 |  | 0.0215 |  | 1.4896e-08 |  | 0.5375 |  | 0.5375 |  | 0.1075 |  | 0.1075 | 92355 |  | 0.064135 |  | 0.064135 |  | 3.5719e-09 |  | 1.6034 |  | 1.6034 |  | 0.32068 |  | 0.32068 | 176560 |  | 0.12261 |  | 0.12261 |  | 8.4952e-08 |  | 3.0653 |  | 3.0653 |  | 0.61306 |  | 0.61306 | 48590 |  | 0.033743 |  | 0.033743 |  | 5.2307e-11 |  | 0.84358 |  | 0.84358 |  | 0.16872 |  | 0.16872 | 10770 |  | 0.0074792 |  | 0.0074792 |  | 3.6441e-12 |  | 0.18698 |  | 0.18698 |  | 0.037396 |  | 0.037396 | 359235 |  | 0.24947 |  | 0.24947 |  | 1.2155e-10 |  | 6.2367 |  | 6.2367 | 0 | 1.2473 | 0 | 1.2473
DSDRC-092 | c | 4DRG | DAPjm | Feeder Regulator | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator sensor data request to Feeder Regulator | FeederRegulator_sensor_data_cmd | cmd | 1 - 7PM | 1 per ¦ fdrVR per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x min |  |  | X | down |  | x | DSDRC-001 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 150 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.18704 |  | 0.18704 |  | 6.25e-08 |  | 28.0558 |  | 28.0558 |  | 0.56112 |  | 0.56112 | 461.2359 |  | 0.51248 |  | 0.51248 |  | 3.3333e-08 |  | 76.8726 |  | 76.8726 |  | 1.5375 |  | 1.5375 | 197.4792 |  | 0.21942 |  | 0.21942 |  | 2.0408e-09 |  | 32.9132 |  | 32.9132 |  | 0.65826 |  | 0.65826 | 137.437 |  | 0.15271 |  | 0.15271 |  | 4.4643e-10 |  | 22.9062 |  | 22.9062 |  | 0.45812 |  | 0.45812 | 964.4867 |  | 1.0717 |  | 1.0717 |  | 3.1329e-09 |  | 160.7478 |  | 160.7478 | 0 | 3.215 | 0 | 3.215
DSDRC-093 | c | 4DRG | Feeder Regulator | DAPjm | DSDR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator sensor data reply to DAPjm | FeederRegulator_sensor_data_resp-data | resp-data | 1 - 7PM | 1 per ¦ fdrVR per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 1000 | x min |  |  | X | up |  | x | DSDRC-004 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 0.75 | 1000 | 4 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.18704 |  | 0.74815 |  | 4.1667e-07 |  | 187.0385 |  | 193.7718 |  | 0.56112 |  | 0.56112 | 461.2359 |  | 0.51248 |  | 2.0499 |  | 2.2222e-07 |  | 512.4843 |  | 530.9337 |  | 1.5375 |  | 1.5375 | 197.4792 |  | 0.21942 |  | 0.87769 |  | 1.3605e-08 |  | 219.4213 |  | 227.3205 |  | 0.65826 |  | 0.65826 | 137.437 |  | 0.15271 |  | 0.61083 |  | 2.9762e-09 |  | 152.7078 |  | 158.2053 |  | 0.45812 |  | 0.45812 | 964.4867 |  | 1.0717 |  | 4.2866 |  | 2.0886e-08 |  | 1071.6518 |  | 1110.2313 | 0 | 3.215 | 0 | 3.215
DSDRC-120 | c | 4DRG | DAPjm | Feeder Regulator | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator step up command to Feeder Regulator | FeederRegulator_step_up_cmd | cmd | 1 - 7PM | 1 per ¦ fdrVR per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 250 | x min |  |  | X | down |  | x | DSDRC-007 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 250 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.56112 |  | 0.56112 |  | 3.125e-07 |  | 140.2788 |  | 140.2788 |  | 1.6833 |  | 1.6833 | 461.2359 |  | 1.5375 |  | 1.5375 |  | 1.6667e-07 |  | 384.3632 |  | 384.3632 |  | 4.6124 |  | 4.6124 | 197.4792 |  | 0.65826 |  | 0.65826 |  | 1.0204e-08 |  | 164.566 |  | 164.566 |  | 1.9748 |  | 1.9748 | 137.437 |  | 0.45812 |  | 0.45812 |  | 2.2321e-09 |  | 114.5308 |  | 114.5308 |  | 1.3744 |  | 1.3744 | 964.4867 |  | 3.215 |  | 3.215 |  | 1.5664e-08 |  | 803.7389 |  | 803.7389 | 0 | 9.6449 | 0 | 9.6449
DSDRC-121 | c | 4DRG | Feeder Regulator | DAPjm | DSDR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator step up command ACK to DAPjm | FeederRegulator_step_up_ack | ack | 1 - 7PM | 1 per ¦ fdrVR per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x min |  |  | X | up |  | x | DSDRC-010 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.56112 |  | 0.56112 |  | 3.125e-08 |  | 14.0279 |  | 14.0279 |  | 1.6833 |  | 1.6833 | 461.2359 |  | 1.5375 |  | 1.5375 |  | 1.6667e-08 |  | 38.4363 |  | 38.4363 |  | 4.6124 |  | 4.6124 | 197.4792 |  | 0.65826 |  | 0.65826 |  | 1.0204e-09 |  | 16.4566 |  | 16.4566 |  | 1.9748 |  | 1.9748 | 137.437 |  | 0.45812 |  | 0.45812 |  | 2.2321e-10 |  | 11.4531 |  | 11.4531 |  | 1.3744 |  | 1.3744 | 964.4867 |  | 3.215 |  | 3.215 |  | 1.5664e-09 |  | 80.3739 |  | 80.3739 | 0 | 9.6449 | 0 | 9.6449
DSDRC-148 | c | 4DRG | DAPjm | Feeder Regulator | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator step down command to Feeder Regulator | FeederRegulator_step_down_cmd | cmd | 1 - 7PM | 1 per ¦ fdrVR per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 250 | x min |  |  | X | down |  | x | DSDRC-013 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 250 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.56112 |  | 0.56112 |  | 3.125e-07 |  | 140.2788 |  | 140.2788 |  | 1.6833 |  | 1.6833 | 461.2359 |  | 1.5375 |  | 1.5375 |  | 1.6667e-07 |  | 384.3632 |  | 384.3632 |  | 4.6124 |  | 4.6124 | 197.4792 |  | 0.65826 |  | 0.65826 |  | 1.0204e-08 |  | 164.566 |  | 164.566 |  | 1.9748 |  | 1.9748 | 137.437 |  | 0.45812 |  | 0.45812 |  | 2.2321e-09 |  | 114.5308 |  | 114.5308 |  | 1.3744 |  | 1.3744 | 964.4867 |  | 3.215 |  | 3.215 |  | 1.5664e-08 |  | 803.7389 |  | 803.7389 | 0 | 9.6449 | 0 | 9.6449
DSDRC-149 | c | 4DRG | Feeder Regulator | DAPjm | DSDR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator step down command ACK to DAPjm | FeederRegulator_step_down_ack | ack | 1 - 7PM | 1 per ¦ fdrVR per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x min |  |  | X | up |  | x | DSDRC-016 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.56112 |  | 0.56112 |  | 3.125e-08 |  | 14.0279 |  | 14.0279 |  | 1.6833 |  | 1.6833 | 461.2359 |  | 1.5375 |  | 1.5375 |  | 1.6667e-08 |  | 38.4363 |  | 38.4363 |  | 4.6124 |  | 4.6124 | 197.4792 |  | 0.65826 |  | 0.65826 |  | 1.0204e-09 |  | 16.4566 |  | 16.4566 |  | 1.9748 |  | 1.9748 | 137.437 |  | 0.45812 |  | 0.45812 |  | 2.2321e-10 |  | 11.4531 |  | 11.4531 |  | 1.3744 |  | 1.3744 | 964.4867 |  | 3.215 |  | 3.215 |  | 1.5664e-09 |  | 80.3739 |  | 80.3739 | 0 | 9.6449 | 0 | 9.6449
DSDRC-176 | c | 4DRG | DAPjm | Feeder Regulator | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator new config to Feeder Regulator | FeederRegulator_new_config_cmd | cmd | 1 - 7PM | 1 per ¦ fdrVR per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 500 | x hour |  |  | X | down |  | x | DSDRC-019 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 1.5 | 500 | 2 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.04676 |  | 0.093519 |  | 5.2083e-08 |  | 23.3798 |  | 24.2215 |  | 0.14028 |  | 0.14028 | 461.2359 |  | 0.12812 |  | 0.25624 |  | 2.7778e-08 |  | 64.0605 |  | 66.3667 |  | 0.38436 |  | 0.38436 | 197.4792 |  | 0.054855 |  | 0.10971 |  | 1.7007e-09 |  | 27.4277 |  | 28.4151 |  | 0.16457 |  | 0.16457 | 137.437 |  | 0.038177 |  | 0.076354 |  | 3.7202e-10 |  | 19.0885 |  | 19.7757 |  | 0.11453 |  | 0.11453 | 964.4867 |  | 0.26791 |  | 0.53583 |  | 2.6107e-09 |  | 133.9565 |  | 138.7789 | 0 | 0.80374 | 0 | 0.80374
DSDRC-177 | c | 4DRG | Feeder Regulator | DAPjm | DSDR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator new config ACK to DAPjm | FeederRegulator_new_config_ack | ack | 1 - 7PM | 1 per ¦ fdrVR per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-022 |  |  | 0.16667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.04676 |  | 0.04676 |  | 2.6042e-09 |  | 1.169 |  | 1.169 |  | 0.14028 |  | 0.14028 | 461.2359 |  | 0.12812 |  | 0.12812 |  | 1.3889e-09 |  | 3.203 |  | 3.203 |  | 0.38436 |  | 0.38436 | 197.4792 |  | 0.054855 |  | 0.054855 |  | 8.5034e-11 |  | 1.3714 |  | 1.3714 |  | 0.16457 |  | 0.16457 | 137.437 |  | 0.038177 |  | 0.038177 |  | 1.8601e-11 |  | 0.95442 |  | 0.95442 |  | 0.11453 |  | 0.11453 | 964.4867 |  | 0.26791 |  | 0.26791 |  | 1.3054e-10 |  | 6.6978 |  | 6.6978 | 0 | 0.80374 | 0 | 0.80374
DSDRC-204 | c | 4DCB | DAPjm | Feeder Cap Bank | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank sensor data request to Feeder Cap Bank | FeederCapBank_sensor_data_cmd | cmd | 1 - 7PM | 1 per ¦ fdrCB per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 50 | x min |  |  | X | down |  | x | DSDRC-025 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.99754 |  | 0.99754 |  | 1.1111e-07 |  | 49.8769 |  | 49.8769 |  | 2.9926 |  | 2.9926 | 2459.9246 |  | 2.7332 |  | 2.7332 |  | 5.9259e-08 |  | 136.6625 |  | 136.6625 |  | 8.1997 |  | 8.1997 | 1053.2224 |  | 1.1702 |  | 1.1702 |  | 3.6281e-09 |  | 58.5124 |  | 58.5124 |  | 3.5107 |  | 3.5107 | 732.9974 |  | 0.81444 |  | 0.81444 |  | 7.9365e-10 |  | 40.7221 |  | 40.7221 |  | 2.4433 |  | 2.4433 | 5143.9289 |  | 5.7155 |  | 5.7155 |  | 5.5696e-09 |  | 285.7738 |  | 285.7738 | 0 | 17.1464 | 0 | 17.1464
DSDRC-205 | c | 4DCB | Feeder Cap Bank | DAPjm | DSDR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank sensor data reply to DAPjm | FeederCapBank_sensor_data_resp-data | resp-data | 1 - 7PM | 1 per ¦ fdrCB per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 100 | x min |  |  | X | up |  | x | DSDRC-028 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 100 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.99754 |  | 0.99754 |  | 2.2222e-07 |  | 99.7538 |  | 99.7538 |  | 2.9926 |  | 2.9926 | 2459.9246 |  | 2.7332 |  | 2.7332 |  | 1.1852e-07 |  | 273.325 |  | 273.325 |  | 8.1997 |  | 8.1997 | 1053.2224 |  | 1.1702 |  | 1.1702 |  | 7.2562e-09 |  | 117.0247 |  | 117.0247 |  | 3.5107 |  | 3.5107 | 732.9974 |  | 0.81444 |  | 0.81444 |  | 1.5873e-09 |  | 81.4442 |  | 81.4442 |  | 2.4433 |  | 2.4433 | 5143.9289 |  | 5.7155 |  | 5.7155 |  | 1.1139e-08 |  | 571.5477 |  | 571.5477 | 0 | 17.1464 | 0 | 17.1464
DSDRC-232 | c | 4DCB | DAPjm | Feeder Cap Bank | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank open command to Feeder Cap Bank | FeederCapBank_open_cmd | cmd | 1 - 7PM | 1 per ¦ fdrCB per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x min |  |  | X | down |  | x | DSDRC-031 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 150 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 |  | 2.9926 |  | 2.9926 |  | 1e-06 |  | 448.8923 |  | 448.8923 |  | 8.9778 |  | 8.9778 | 2459.9246 |  | 8.1997 |  | 8.1997 |  | 5.3333e-07 |  | 1229.9623 |  | 1229.9623 |  | 24.5992 |  | 24.5992 | 1053.2224 |  | 3.5107 |  | 3.5107 |  | 3.2653e-08 |  | 526.6112 |  | 526.6112 |  | 10.5322 |  | 10.5322 | 732.9974 |  | 2.4433 |  | 2.4433 |  | 7.1429e-09 |  | 366.4987 |  | 366.4987 |  | 7.33 |  | 7.33 | 5143.9289 |  | 17.1464 |  | 17.1464 |  | 5.0126e-08 |  | 2571.9644 |  | 2571.9644 | 0 | 51.4393 | 0 | 51.4393
DSDRC-233 | c | 4DCB | Feeder Cap Bank | DAPjm | DSDR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank open command ACK to DAPjm | FeederCapBank_open_ack | ack | 1 - 7PM | 1 per ¦ fdrCB per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x min |  |  | X | up |  | x | DSDRC-034 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 |  | 2.9926 |  | 2.9926 |  | 1.6667e-07 |  | 74.8154 |  | 74.8154 |  | 8.9778 |  | 8.9778 | 2459.9246 |  | 8.1997 |  | 8.1997 |  | 8.8889e-08 |  | 204.9937 |  | 204.9937 |  | 24.5992 |  | 24.5992 | 1053.2224 |  | 3.5107 |  | 3.5107 |  | 5.4422e-09 |  | 87.7685 |  | 87.7685 |  | 10.5322 |  | 10.5322 | 732.9974 |  | 2.4433 |  | 2.4433 |  | 1.1905e-09 |  | 61.0831 |  | 61.0831 |  | 7.33 |  | 7.33 | 5143.9289 |  | 17.1464 |  | 17.1464 |  | 8.3544e-09 |  | 428.6607 |  | 428.6607 | 0 | 51.4393 | 0 | 51.4393
DSDRC-260 | c | 4DCB | DAPjm | Feeder Cap Bank | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank close command to Feeder Cap Bank | FeederCapBank_close_cmd | cmd | 1 - 7PM | 1 per ¦ fdrCB per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x min |  |  | X | down |  | x | DSDRC-037 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 150 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 |  | 2.9926 |  | 2.9926 |  | 1e-06 |  | 448.8923 |  | 448.8923 |  | 8.9778 |  | 8.9778 | 2459.9246 |  | 8.1997 |  | 8.1997 |  | 5.3333e-07 |  | 1229.9623 |  | 1229.9623 |  | 24.5992 |  | 24.5992 | 1053.2224 |  | 3.5107 |  | 3.5107 |  | 3.2653e-08 |  | 526.6112 |  | 526.6112 |  | 10.5322 |  | 10.5322 | 732.9974 |  | 2.4433 |  | 2.4433 |  | 7.1429e-09 |  | 366.4987 |  | 366.4987 |  | 7.33 |  | 7.33 | 5143.9289 |  | 17.1464 |  | 17.1464 |  | 5.0126e-08 |  | 2571.9644 |  | 2571.9644 | 0 | 51.4393 | 0 | 51.4393
DSDRC-261 | c | 4DCB | Feeder Cap Bank | DAPjm | DSDR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank close command ACK to DAPjm | FeederCapBank_close_ack | ack | 1 - 7PM | 1 per ¦ fdrCB per ¦ 5 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x min |  |  | X | up |  | x | DSDRC-040 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 |  | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 |  | 2.9926 |  | 2.9926 |  | 1.6667e-07 |  | 74.8154 |  | 74.8154 |  | 8.9778 |  | 8.9778 | 2459.9246 |  | 8.1997 |  | 8.1997 |  | 8.8889e-08 |  | 204.9937 |  | 204.9937 |  | 24.5992 |  | 24.5992 | 1053.2224 |  | 3.5107 |  | 3.5107 |  | 5.4422e-09 |  | 87.7685 |  | 87.7685 |  | 10.5322 |  | 10.5322 | 732.9974 |  | 2.4433 |  | 2.4433 |  | 1.1905e-09 |  | 61.0831 |  | 61.0831 |  | 7.33 |  | 7.33 | 5143.9289 |  | 17.1464 |  | 17.1464 |  | 8.3544e-09 |  | 428.6607 |  | 428.6607 | 0 | 51.4393 | 0 | 51.4393
DSDRC-288 | c | 4DCB | DAPjm | Feeder Cap Bank | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank new config to Feeder Cap Bank | FeederCapBank_new_config_cmd | cmd | 1 - 7PM | 1 per ¦ fdrCB per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 500 | x hour |  |  | X | down |  | x | DSDRC-043 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 1.5 | 500 | 2 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.24938 |  | 0.49877 |  | 2.7778e-07 |  | 124.6923 |  | 129.1812 |  | 0.74815 |  | 0.74815 | 2459.9246 |  | 0.68331 |  | 1.3666 |  | 1.4815e-07 |  | 341.6562 |  | 353.9558 |  | 2.0499 |  | 2.0499 | 1053.2224 |  | 0.29256 |  | 0.58512 |  | 9.0703e-09 |  | 146.2809 |  | 151.547 |  | 0.87769 |  | 0.87769 | 732.9974 |  | 0.20361 |  | 0.40722 |  | 1.9841e-09 |  | 101.8052 |  | 105.4702 |  | 0.61083 |  | 0.61083 | 5143.9289 |  | 1.4289 |  | 2.8577 |  | 1.3924e-08 |  | 714.4346 |  | 740.1542 | 0 | 4.2866 | 0 | 4.2866
DSDRC-289 | c | 4DCB | Feeder Cap Bank | DAPjm | DSDR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank new config ACK to DAPjm | FeederCapBank_new_config_ack | ack | 1 - 7PM | 1 per ¦ fdrCB per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-046 |  |  | 0.16667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.24938 |  | 0.24938 |  | 1.3889e-08 |  | 6.2346 |  | 6.2346 |  | 0.74815 |  | 0.74815 | 2459.9246 |  | 0.68331 |  | 0.68331 |  | 7.4074e-09 |  | 17.0828 |  | 17.0828 |  | 2.0499 |  | 2.0499 | 1053.2224 |  | 0.29256 |  | 0.29256 |  | 4.5351e-10 |  | 7.314 |  | 7.314 |  | 0.87769 |  | 0.87769 | 732.9974 |  | 0.20361 |  | 0.20361 |  | 9.9206e-11 |  | 5.0903 |  | 5.0903 |  | 0.61083 |  | 0.61083 | 5143.9289 |  | 1.4289 |  | 1.4289 |  | 6.962e-10 |  | 35.7217 |  | 35.7217 | 0 | 4.2866 | 0 | 4.2866
DSDRC-316 | c | 4DS | DAPjm | Feeder Sensor | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Sensor data request to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | 1 - 7PM | 1 per ¦ fdrFS per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x min |  |  | X | down |  | x | DSDRC-049 |  |  | 0.16667 | 1 | fdrFS | fdrFS | 3 | 3 | 150 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 1.2469 |  | 1.2469 |  | 4.1667e-07 |  | 187.0385 |  | 187.0385 |  | 3.7408 |  | 3.7408 | 3074.9057 |  | 3.4166 |  | 3.4166 |  | 2.2222e-07 |  | 512.4843 |  | 512.4843 |  | 10.2497 |  | 10.2497 | 1316.5279 |  | 1.4628 |  | 1.4628 |  | 1.3605e-08 |  | 219.4213 |  | 219.4213 |  | 4.3884 |  | 4.3884 | 916.2467 |  | 1.0181 |  | 1.0181 |  | 2.9762e-09 |  | 152.7078 |  | 152.7078 |  | 3.0542 |  | 3.0542 | 6429.9111 |  | 7.1443 |  | 7.1443 |  | 2.0886e-08 |  | 1071.6518 |  | 1071.6518 | 0 | 21.433 | 0 | 21.433
DSDRC-317 | c | 4DS | Feeder Sensor | DAPjm | DSDR - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor data reply to DAPjm | FeederSensor_sensor_data_resp-data | resp-data | 1 - 7PM | 1 per ¦ fdrFS per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 250 | x min |  |  | X | up |  | x | DSDRC-052 |  |  | 0.16667 | 1 | fdrFS | fdrFS | 3 | 3 | 250 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 1.2469 |  | 1.2469 |  | 6.9444e-07 |  | 311.7308 |  | 311.7308 |  | 3.7408 |  | 3.7408 | 3074.9057 |  | 3.4166 |  | 3.4166 |  | 3.7037e-07 |  | 854.1405 |  | 854.1405 |  | 10.2497 |  | 10.2497 | 1316.5279 |  | 1.4628 |  | 1.4628 |  | 2.2676e-08 |  | 365.7022 |  | 365.7022 |  | 4.3884 |  | 4.3884 | 916.2467 |  | 1.0181 |  | 1.0181 |  | 4.9603e-09 |  | 254.513 |  | 254.513 |  | 3.0542 |  | 3.0542 | 6429.9111 |  | 7.1443 |  | 7.1443 |  | 3.481e-08 |  | 1786.0864 |  | 1786.0864 | 0 | 21.433 | 0 | 21.433
DSDRC-344 | c | 4DS | DAPjm | Feeder Sensor | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Sensor new config to Feeder Sensor | FeederSensor_new_config_cmd | cmd | 1 - 7PM | 1 per ¦ fdrFS per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 500 | x hour |  |  | X | down |  | x | DSDRC-055 |  |  | 0.16667 | 1 | fdrFS | fdrFS | 3 | 1.5 | 500 | 2 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.31173 |  | 0.62346 |  | 3.4722e-07 |  | 155.8654 |  | 161.4765 |  | 0.93519 |  | 0.93519 | 3074.9057 |  | 0.85414 |  | 1.7083 |  | 1.8519e-07 |  | 427.0702 |  | 442.4448 |  | 2.5624 |  | 2.5624 | 1316.5279 |  | 0.3657 |  | 0.7314 |  | 1.1338e-08 |  | 182.8511 |  | 189.4337 |  | 1.0971 |  | 1.0971 | 916.2467 |  | 0.25451 |  | 0.50903 |  | 2.4802e-09 |  | 127.2565 |  | 131.8377 |  | 0.76354 |  | 0.76354 | 6429.9111 |  | 1.7861 |  | 3.5722 |  | 1.7405e-08 |  | 893.0432 |  | 925.1928 | 0 | 5.3583 | 0 | 5.3583
DSDRC-345 | c | 4DS | Feeder Sensor | DAPjm | DSDR - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor new config ACK to DAPjm | FeederSensor_new_config_ack | ack | 1 - 7PM | 1 per ¦ fdrFS per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-058 |  |  | 0.16667 | 1 | fdrFS | fdrFS | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.31173 |  | 0.31173 |  | 1.7361e-08 |  | 7.7933 |  | 7.7933 |  | 0.93519 |  | 0.93519 | 3074.9057 |  | 0.85414 |  | 0.85414 |  | 9.2593e-09 |  | 21.3535 |  | 21.3535 |  | 2.5624 |  | 2.5624 | 1316.5279 |  | 0.3657 |  | 0.3657 |  | 5.6689e-10 |  | 9.1426 |  | 9.1426 |  | 1.0971 |  | 1.0971 | 916.2467 |  | 0.25451 |  | 0.25451 |  | 1.2401e-10 |  | 6.3628 |  | 6.3628 |  | 0.76354 |  | 0.76354 | 6429.9111 |  | 1.7861 |  | 1.7861 |  | 8.7025e-10 |  | 44.6522 |  | 44.6522 | 0 | 5.3583 | 0 | 5.3583
DSDRC-372 | c | 4DSW | DAPjm | Feeder Switch | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Switch sensor data request to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | 1 - 7PM | 1 per ¦ fdrSW per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 50 | x min |  |  | X | down |  | x | DSDRC-061 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.49877 |  | 0.49877 |  | 5.5556e-08 |  | 24.9385 |  | 24.9385 |  | 1.4963 |  | 1.4963 | 1229.9623 |  | 1.3666 |  | 1.3666 |  | 2.963e-08 |  | 68.3312 |  | 68.3312 |  | 4.0999 |  | 4.0999 | 526.6112 |  | 0.58512 |  | 0.58512 |  | 1.8141e-09 |  | 29.2562 |  | 29.2562 |  | 1.7554 |  | 1.7554 | 366.4987 |  | 0.40722 |  | 0.40722 |  | 3.9683e-10 |  | 20.361 |  | 20.361 |  | 1.2217 |  | 1.2217 | 2571.9644 |  | 2.8577 |  | 2.8577 |  | 2.7848e-09 |  | 142.8869 |  | 142.8869 | 0 | 8.5732 | 0 | 8.5732
DSDRC-373 | c | 4DSW | Feeder Switch | DAPjm | DSDR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch sensor data reply to DAPjm | FeederSwitch_sensor_data_resp-data | resp-data | 1 - 7PM | 1 per ¦ fdrSW per ¦ 15 min ¦ 4-8 times per year | > 99.5% | < 3 sec | 100 | x min |  |  | X | up |  | x | DSDRC-064 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 100 | 1 |  | 0.0011111 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.49877 |  | 0.49877 |  | 1.1111e-07 |  | 49.8769 |  | 49.8769 |  | 1.4963 |  | 1.4963 | 1229.9623 |  | 1.3666 |  | 1.3666 |  | 5.9259e-08 |  | 136.6625 |  | 136.6625 |  | 4.0999 |  | 4.0999 | 526.6112 |  | 0.58512 |  | 0.58512 |  | 3.6281e-09 |  | 58.5124 |  | 58.5124 |  | 1.7554 |  | 1.7554 | 366.4987 |  | 0.40722 |  | 0.40722 |  | 7.9365e-10 |  | 40.7221 |  | 40.7221 |  | 1.2217 |  | 1.2217 | 2571.9644 |  | 2.8577 |  | 2.8577 |  | 5.5696e-09 |  | 285.7738 |  | 285.7738 | 0 | 8.5732 | 0 | 8.5732
DSDRC-402 | c | 4DSW | DAPjm | Feeder Switch | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Switch open command to Feeder Switch | FeederSwitch_open_cmd | cmd | 1 - 7PM | 1 per ¦ fdrSW per ¦ 12 hours ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x hour |  |  | X | down |  | x | DSDRC-067 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 150 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.12469 |  | 4.1667e-08 |  | 18.7038 |  | 18.7038 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.34166 |  | 2.2222e-08 |  | 51.2484 |  | 51.2484 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.14628 |  | 1.3605e-09 |  | 21.9421 |  | 21.9421 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.10181 |  | 2.9762e-10 |  | 15.2708 |  | 15.2708 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 0.71443 |  | 2.0886e-09 |  | 107.1652 |  | 107.1652 | 0 | 2.1433 | 0 | 2.1433
DSDRC-403 | c | 4DSW | Feeder Switch | DAPjm | DSDR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch open command ACK to DAPjm | FeederSwitch_open_ack | ack | 1 - 7PM | 1 per ¦ fdrSW per ¦ 12 hours ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-070 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.12469 |  | 6.9444e-09 |  | 3.1173 |  | 3.1173 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.34166 |  | 3.7037e-09 |  | 8.5414 |  | 8.5414 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.14628 |  | 2.2676e-10 |  | 3.657 |  | 3.657 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.10181 |  | 4.9603e-11 |  | 2.5451 |  | 2.5451 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 0.71443 |  | 3.481e-10 |  | 17.8609 |  | 17.8609 | 0 | 2.1433 | 0 | 2.1433
DSDRC-430 | c | 4DSW | DAPjm | Feeder Switch | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Switch close command to Feeder Switch | FeederSwitch_close_cmd | cmd | 1 - 7PM | 1 per ¦ fdrSW per ¦ 12 hours ¦ 4-8 times per year | > 99.5% | < 3 sec | 150 | x hour |  |  | X | down |  | x | DSDRC-073 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 150 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.12469 |  | 4.1667e-08 |  | 18.7038 |  | 18.7038 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.34166 |  | 2.2222e-08 |  | 51.2484 |  | 51.2484 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.14628 |  | 1.3605e-09 |  | 21.9421 |  | 21.9421 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.10181 |  | 2.9762e-10 |  | 15.2708 |  | 15.2708 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 0.71443 |  | 2.0886e-09 |  | 107.1652 |  | 107.1652 | 0 | 2.1433 | 0 | 2.1433
DSDRC-431 | c | 4DSW | Feeder Switch | DAPjm | DSDR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch close command ACK to DAPjm | FeederSwitch_close_ack | ack | 1 - 7PM | 1 per ¦ fdrSW per ¦ 12 hours ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-076 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.12469 |  | 6.9444e-09 |  | 3.1173 |  | 3.1173 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.34166 |  | 3.7037e-09 |  | 8.5414 |  | 8.5414 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.14628 |  | 2.2676e-10 |  | 3.657 |  | 3.657 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.10181 |  | 4.9603e-11 |  | 2.5451 |  | 2.5451 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 0.71443 |  | 3.481e-10 |  | 17.8609 |  | 17.8609 | 0 | 2.1433 | 0 | 2.1433
DSDRC-448 | c | 4DSW | Feeder Switch | DAPjm | DSDR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch new config ACK to DAPjm | FeederSwitch_new_config_ack | ack | 1 - 7PM | 1 per ¦ fdrSW per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 25 | x hour |  |  | X | up |  | x | DSDRC-445 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.12469 |  | 6.9444e-09 |  | 3.1173 |  | 3.1173 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.34166 |  | 3.7037e-09 |  | 8.5414 |  | 8.5414 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.14628 |  | 2.2676e-10 |  | 3.657 |  | 3.657 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.10181 |  | 4.9603e-11 |  | 2.5451 |  | 2.5451 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 0.71443 |  | 3.481e-10 |  | 17.8609 |  | 17.8609 | 0 | 2.1433 | 0 | 2.1433
DSDRC-478 | c | 4DSW | DAPjm | Feeder Switch | DSDR - Centralized Control | DAPjm may be able to process & forward Feeder Switch new config to Feeder Switch | FeederSwitch_new_config_cmd | cmd | 1 - 7PM | 1 per ¦ fdrSW per ¦ hour ¦ 4-8 times per year | > 99.5% | < 3 sec | 500 | x hour |  |  | X | down |  | x | DSDRC-462 |  |  | 0.16667 | 1 | fdrSW | fdrSW | 3 | 1.5 | 500 | 2 |  | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.12469 |  | 0.24938 |  | 1.3889e-07 |  | 62.3462 |  | 64.5906 |  | 0.37408 |  | 0.37408 | 1229.9623 |  | 0.34166 |  | 0.68331 |  | 7.4074e-08 |  | 170.8281 |  | 176.9779 |  | 1.025 |  | 1.025 | 526.6112 |  | 0.14628 |  | 0.29256 |  | 4.5351e-09 |  | 73.1404 |  | 75.7735 |  | 0.43884 |  | 0.43884 | 366.4987 |  | 0.10181 |  | 0.20361 |  | 9.9206e-10 |  | 50.9026 |  | 52.7351 |  | 0.30542 |  | 0.30542 | 2571.9644 |  | 0.71443 |  | 1.4289 |  | 6.962e-09 |  | 357.2173 |  | 370.0771 | 0 | 2.1433 | 0 | 2.1433
FCIR-x1 | c | 4FRC | FAN gateway - field | Feeder Recloser | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Recloser | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ x zone isolation step within < 30sec of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-012 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x2 | c | 4FSW | FAN gateway - field | Feeder Switch | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Switch | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ x zone isolation step within < 30sec of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-012 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x3 | c | 4FST | FAN gateway - field | Feeder Sectionalizer | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Sectionalizer | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST per ¦ x zone isolation step within < 30sec of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-012 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x5 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ x zone isolation step within < 1 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-020 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x6 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ x zone isolation step within < 1 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-020 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x7 | c | 4FST | Feeder Sectionalizer | FAN gateway - field | FCIR - DMS | Feeder Sectionalizer shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST per ¦ x zone isolation step within < 1 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-020 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x9 | c | 4FRC | FAN gateway - field | Feeder Recloser | FCIR - DMS | FAN gateway - field shall be able to process & forward device operate request to appropriate Feeder Recloser | circuit_device_oper_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 1.5 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-028 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x10 | c | 4FSW | FAN gateway - field | Feeder Switch | FCIR - DMS | FAN gateway - field shall be able to process & forward device operate request to appropriate Feeder Switch | circuit_device_oper_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 1.5 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-028 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x11 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to send operate device acknowledgement to FAN gateway - field | circuit_device_oper_cmd_ack | ack | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 1.5 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | up |  | x | FCIR-C-034 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x12 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to send operate device acknowledgement to FAN gateway - field | circuit_device_oper_cmd_ack | ack | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 1.5 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | up |  | x | FCIR-C-034 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x13 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to process & send device self inititated status response data to FAN gateway - field | circuit_device_self-init_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 2 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-040 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x14 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to process & send device self initiated status response data to FAN gateway - field | circuit_device_self-init_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 2 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-040 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x15 | c | 4FRC | FAN gateway - field | Feeder Recloser | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Recloser | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC per ¦ x circuit reconfig step within < 2 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-046 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 504 | 1.5982e-05 | 0.023333 | 1.5982e-05 | 0.023333 | 1.7801e-12 | 2.599e-09 | 0.00079909 | 1.1667 | 0.00079909 | 1.1667 | 4.7945e-05 | 0.07 | 4.7945e-05 | 0.07 | 1751.8 | 5.5549e-05 | 0.081102 | 5.5549e-05 | 0.081102 | 1.2044e-12 | 1.7584e-09 | 0.0027775 | 4.0551 | 0.0027775 | 4.0551 | 0.00016665 | 0.24331 | 0.00016665 | 0.24331 | 84 | 2.6636e-06 | 0.0038889 | 2.6636e-06 | 0.0038889 | 8.258e-15 | 1.2057e-11 | 0.00013318 | 0.19444 | 0.00013318 | 0.19444 | 7.9909e-06 | 0.011667 | 7.9909e-06 | 0.011667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2339.8 | 7.4195e-05 | 0.10832 | 7.4195e-05 | 0.10832 | 7.2301e-14 | 1.0556e-10 | 0.0037097 | 5.4162 | 0.0037097 | 5.4162 | 0.00022258 | 0.32497 | 0.00022258 | 0.32497
FCIR-x16 | c | 4FSW | FAN gateway - field | Feeder Switch | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Switch | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW per ¦ x circuit reconfig step within < 2 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-046 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 336 | 1.0654e-05 | 0.015556 | 1.0654e-05 | 0.015556 | 1.1868e-12 | 1.7327e-09 | 0.00053272 | 0.77778 | 0.00053272 | 0.77778 | 3.1963e-05 | 0.046667 | 3.1963e-05 | 0.046667 | 1166.6 | 3.6993e-05 | 0.054009 | 3.6993e-05 | 0.054009 | 8.0203e-13 | 1.171e-09 | 0.0018496 | 2.7005 | 0.0018496 | 2.7005 | 0.00011098 | 0.16203 | 0.00011098 | 0.16203 | 54.6 | 1.7314e-06 | 0.0025278 | 1.7314e-06 | 0.0025278 | 5.3677e-15 | 7.8369e-12 | 8.6568e-05 | 0.12639 | 8.6568e-05 | 0.12639 | 5.1941e-06 | 0.0075833 | 5.1941e-06 | 0.0075833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1557.2 | 4.9378e-05 | 0.072093 | 4.9378e-05 | 0.072093 | 4.8118e-14 | 7.0252e-11 | 0.0024689 | 3.6046 | 0.0024689 | 3.6046 | 0.00014814 | 0.21628 | 0.00014814 | 0.21628
FCIR-x17 | c | 4FST | FAN gateway - field | Feeder Sectionalizer | FCIR - DMS | FAN gateway - field shall be able to process & forward device status request to Feeder Sectionalizer | circuit_device_status_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST per ¦ x circuit reconfig step within < 2 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-046 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x19 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC per ¦ x circuit reconfig step within < 2.5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-054 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 504 | 1.5982e-05 | 0.023333 | 1.5982e-05 | 0.023333 | 1.7801e-12 | 2.599e-09 | 0.00079909 | 1.1667 | 0.00079909 | 1.1667 | 4.7945e-05 | 0.07 | 4.7945e-05 | 0.07 | 1751.8 | 5.5549e-05 | 0.081102 | 5.5549e-05 | 0.081102 | 1.2044e-12 | 1.7584e-09 | 0.0027775 | 4.0551 | 0.0027775 | 4.0551 | 0.00016665 | 0.24331 | 0.00016665 | 0.24331 | 84 | 2.6636e-06 | 0.0038889 | 2.6636e-06 | 0.0038889 | 8.258e-15 | 1.2057e-11 | 0.00013318 | 0.19444 | 0.00013318 | 0.19444 | 7.9909e-06 | 0.011667 | 7.9909e-06 | 0.011667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2339.8 | 7.4195e-05 | 0.10832 | 7.4195e-05 | 0.10832 | 7.2301e-14 | 1.0556e-10 | 0.0037097 | 5.4162 | 0.0037097 | 5.4162 | 0.00022258 | 0.32497 | 0.00022258 | 0.32497
FCIR-x20 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW per ¦ x circuit reconfig step within < 2.5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-054 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 336 | 1.0654e-05 | 0.015556 | 1.0654e-05 | 0.015556 | 1.1868e-12 | 1.7327e-09 | 0.00053272 | 0.77778 | 0.00053272 | 0.77778 | 3.1963e-05 | 0.046667 | 3.1963e-05 | 0.046667 | 1166.6 | 3.6993e-05 | 0.054009 | 3.6993e-05 | 0.054009 | 8.0203e-13 | 1.171e-09 | 0.0018496 | 2.7005 | 0.0018496 | 2.7005 | 0.00011098 | 0.16203 | 0.00011098 | 0.16203 | 54.6 | 1.7314e-06 | 0.0025278 | 1.7314e-06 | 0.0025278 | 5.3677e-15 | 7.8369e-12 | 8.6568e-05 | 0.12639 | 8.6568e-05 | 0.12639 | 5.1941e-06 | 0.0075833 | 5.1941e-06 | 0.0075833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1557.2 | 4.9378e-05 | 0.072093 | 4.9378e-05 | 0.072093 | 4.8118e-14 | 7.0252e-11 | 0.0024689 | 3.6046 | 0.0024689 | 3.6046 | 0.00014814 | 0.21628 | 0.00014814 | 0.21628
FCIR-x21 | c | 4FST | Feeder Sectionalizer | FAN gateway - field | FCIR - DMS | Feeder Sectionalizer shall be able to send device status response data to FAN gateway - field | circuit_device_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST per ¦ x circuit reconfig step within < 2.5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-054 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Circuit(y)-reconfig-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x23 | c | 4FRC | FAN gateway - field | Feeder Recloser | FCIR - DMS | FAN gateway - field shall be able to process & forward device operate request to appropriate Feeder Recloser | circuit_device_oper_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-062 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x24 | c | 4FSW | FAN gateway - field | Feeder Switch | FCIR - DMS | FAN gateway - field shall be able to process & forward device operate request to appropriate Feeder Switch | circuit_device_oper_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-062 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x25 | c | 4FST | FAN gateway - field | Feeder Sectionalizer | FCIR - DMS | FAN gateway - field shall be able to process & forward device operate request to appropriate Feeder Sectionalizer | circuit_device_oper_cmd | cmd | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | down |  | x | FCIR-C-062 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x26 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to send operate device acknowledgement to FAN gateway - field | circuit_device_oper_cmd_ack | ack | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | up |  | x | FCIR-C-069 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x27 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to send operate device acknowledgement to FAN gateway - field | circuit_device_oper_cmd_ack | ack | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | up |  | x | FCIR-C-069 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x28 | c | 4FST | Feeder Sectionalizer | FAN gateway - field | FCIR - DMS | Feeder Sectionalizer shall be able to send operate device acknowledgement to FAN gateway - field | circuit_device_oper_cmd_ack | ack | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST per ¦ FCIR reconfig event within < 3 min of fault event | > 99.5% | < 3 sec | 25 | event | ND | X | X | up |  | x | FCIR-C-069 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x29 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to process & send operate device self initiated status response data to FAN gateway - field | circuit_device_self-init_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC per ¦ FCIR reconfig event within < 5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-076 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 303 | 9.6081e-06 | 0.014028 | 9.6081e-06 | 0.014028 | 1.0702e-12 | 1.5625e-09 | 0.0004804 | 0.70139 | 0.0004804 | 0.70139 | 2.8824e-05 | 0.042083 | 2.8824e-05 | 0.042083 | 1052.6 | 3.3378e-05 | 0.048731 | 3.3378e-05 | 0.048731 | 7.2366e-13 | 1.0565e-09 | 0.0016689 | 2.4366 | 0.0016689 | 2.4366 | 0.00010013 | 0.14619 | 0.00010013 | 0.14619 | 50.4 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 4.9548e-15 | 7.234e-12 | 7.9909e-05 | 0.11667 | 7.9909e-05 | 0.11667 | 4.7945e-06 | 0.007 | 4.7945e-06 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1406 | 4.4584e-05 | 0.065093 | 4.4584e-05 | 0.065093 | 4.3446e-14 | 6.3431e-11 | 0.0022292 | 3.2546 | 0.0022292 | 3.2546 | 0.00013375 | 0.19528 | 0.00013375 | 0.19528
FCIR-x30 | c | 4FSW | Feeder Switch | FAN gateway - field | FCIR - DMS | Feeder Switch shall be able to process & send device self initiated status response data to FAN gateway - field | circuit_device_self-init_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW per ¦ FCIR reconfig event within < 5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-076 |  |  | 0.041667 | 1 | fdrSW | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrSW | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 471 | 1.4935e-05 | 0.021806 | 1.4935e-05 | 0.021806 | 1.6636e-12 | 2.4288e-09 | 0.00074677 | 1.0903 | 0.00074677 | 1.0903 | 4.4806e-05 | 0.065417 | 4.4806e-05 | 0.065417 | 1634 | 5.1814e-05 | 0.075648 | 5.1814e-05 | 0.075648 | 1.1234e-12 | 1.6401e-09 | 0.0025907 | 3.7824 | 0.0025907 | 3.7824 | 0.00015544 | 0.22694 | 0.00015544 | 0.22694 | 75.6 | 2.3973e-06 | 0.0035 | 2.3973e-06 | 0.0035 | 7.4322e-15 | 1.0851e-11 | 0.00011986 | 0.175 | 0.00011986 | 0.175 | 7.1918e-06 | 0.0105 | 7.1918e-06 | 0.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2180.6 | 6.9146e-05 | 0.10095 | 6.9146e-05 | 0.10095 | 6.7381e-14 | 9.8377e-11 | 0.0034573 | 5.0477 | 0.0034573 | 5.0477 | 0.00020744 | 0.30286 | 0.00020744 | 0.30286
FCIR-x31 | c | 4FST | Feeder Sectionalizer | FAN gateway - field | FCIR - DMS | Feeder Sectionalizer shall be able to process & send device self initiated status response data to FAN gateway - field | circuit_device_self-init_status_resp-data | resp-data | 24x7 | 1 per ¦ FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST per ¦ FCIR reconfig event within < 5 min of fault event | > 99.5% | < 3 sec | 50 | event | ND | X | X | up |  | x | FCIR-C-076 |  |  | 0.041667 | 1 | fdrST | FldFANgw(x)Sub(x)-Zone(y)-isolate-fdrST | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FCIR-x32 | c | 4FRC | Feeder Recloser | FAN gateway - field | FCIR - DMS | Feeder Recloser shall be able to send fault lock out alarm to FAN gateway - field | fault_lock_out_alarm | alarm | 24x7 | x per ¦ FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrRC per ¦ within < 10sec of fault event | > 99.5% | < 3 sec | 50 | time period | N | X | X | up |  | x | FCIR-C-001 |  |  | 0.041667 | 1 | fdrRC | FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrRC | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 708 | 2.2451e-05 | 0.032778 | 2.2451e-05 | 0.032778 | 2.5007e-12 | 3.651e-09 | 0.0011225 | 1.6389 | 0.0011225 | 1.6389 | 6.7352e-05 | 0.098333 | 6.7352e-05 | 0.098333 | 2804.4 | 8.8927e-05 | 0.12983 | 8.8927e-05 | 0.12983 | 1.928e-12 | 2.8149e-09 | 0.0044463 | 6.4917 | 0.0044463 | 6.4917 | 0.00026678 | 0.3895 | 0.00026678 | 0.3895 | 117.6 | 3.7291e-06 | 0.0054444 | 3.7291e-06 | 0.0054444 | 1.1561e-14 | 1.6879e-11 | 0.00018645 | 0.27222 | 0.00018645 | 0.27222 | 1.1187e-05 | 0.016333 | 1.1187e-05 | 0.016333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3630 | 0.00011511 | 0.16806 | 0.00011511 | 0.16806 | 1.1217e-13 | 1.6377e-10 | 0.0057553 | 8.4028 | 0.0057553 | 8.4028 | 0.00034532 | 0.50417 | 0.00034532 | 0.50417
FCIR-x33 | c | 4FFGa | FAN gateway - sub | FAN gateway - field | FCIR - DMS | FAN gateway - sub shall be able to process & forward fault lock out alarm to FAN gateway - field | fault_lock_out_alarm | alarm | 24x7 | x per ¦ FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrCrtBrk per ¦ within < 10sec of fault event | > 99.5% | < 3 sec | 50 | time period | N | X | X | up |  | x | FCIR-C-001 |  |  | 0.041667 | 1 | fdrCrtBrk | FldFANgw(x)Sub(x)-faulted-Circuit(y)-lockout-fdrCrtBrk | 3 | 3 | 50 | 1 | 3.171e-08 | 4.6296e-05 | [12 empty] | 0 |  | 0 | 201 | 6.3737e-06 | 0.0093056 | 6.3737e-06 | 0.0093056 | 7.0993e-13 | 1.0365e-09 | 0.00031868 | 0.46528 | 0.00031868 | 0.46528 | 1.9121e-05 | 0.027917 | 1.9121e-05 | 0.027917 | 231.8 | 7.3503e-06 | 0.010731 | 7.3503e-06 | 0.010731 | 1.5936e-13 | 2.3267e-10 | 0.00036752 | 0.53657 | 0.00036752 | 0.53657 | 2.2051e-05 | 0.032194 | 2.2051e-05 | 0.032194 | 16.8 | 5.3272e-07 | 0.00077778 | 5.3272e-07 | 0.00077778 | 1.6516e-15 | 2.4113e-12 | 2.6636e-05 | 0.038889 | 2.6636e-05 | 0.038889 | 1.5982e-06 | 0.0023333 | 1.5982e-06 | 0.0023333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449.6 | 1.4257e-05 | 0.020815 | 1.4257e-05 | 0.020815 | 1.3893e-14 | 2.0283e-11 | 0.00071284 | 1.0407 | 0.00071284 | 1.0407 | 4.277e-05 | 0.062444 | 4.277e-05 | 0.062444
FDAMC-152 | c | 4DRG | DAPjm | Feeder Regulator | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Regulator status request to Feeder Regulator | FeederRegulator_status_cmd | cmd | 24x7 | 1 per ¦ fdrVR per ¦ 5 min | > 99.5% | < 3 sec | 50 | x min |  | X | X | down |  | x | FDAMC-001 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 | 0.0033333 | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 | 0.56112 | 0.56112 | 0.56112 | 0.56112 | 6.25e-08 | 6.25e-08 | 28.0558 | 28.0558 | 28.0558 | 28.0558 | 1.6833 | 1.6833 | 1.6833 | 1.6833 | 461.2359 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 3.3333e-08 | 3.3333e-08 | 76.8726 | 76.8726 | 76.8726 | 76.8726 | 4.6124 | 4.6124 | 4.6124 | 4.6124 | 197.4792 | 0.65826 | 0.65826 | 0.65826 | 0.65826 | 2.0408e-09 | 2.0408e-09 | 32.9132 | 32.9132 | 32.9132 | 32.9132 | 1.9748 | 1.9748 | 1.9748 | 1.9748 | 137.437 | 0.45812 | 0.45812 | 0.45812 | 0.45812 | 4.4643e-10 | 4.4643e-10 | 22.9062 | 22.9062 | 22.9062 | 22.9062 | 1.3744 | 1.3744 | 1.3744 | 1.3744 | 964.4867 | 3.215 | 3.215 | 3.215 | 3.215 | 3.1329e-09 | 3.1329e-09 | 160.7478 | 160.7478 | 160.7478 | 160.7478 | 9.6449 | 9.6449 | 9.6449 | 9.6449
FDAMC-153 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator status reply to DAPjm | FeederRegulator_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrVR per ¦ 5 min | > 99.5% | < 3 sec | 50 | x min |  | X | X | up |  | x | FDAMC-004 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 | 0.0033333 | 0.0033333 | [12 empty] | 0 |  | 0 | 168.3346 | 0.56112 | 0.56112 | 0.56112 | 0.56112 | 6.25e-08 | 6.25e-08 | 28.0558 | 28.0558 | 28.0558 | 28.0558 | 1.6833 | 1.6833 | 1.6833 | 1.6833 | 461.2359 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 3.3333e-08 | 3.3333e-08 | 76.8726 | 76.8726 | 76.8726 | 76.8726 | 4.6124 | 4.6124 | 4.6124 | 4.6124 | 197.4792 | 0.65826 | 0.65826 | 0.65826 | 0.65826 | 2.0408e-09 | 2.0408e-09 | 32.9132 | 32.9132 | 32.9132 | 32.9132 | 1.9748 | 1.9748 | 1.9748 | 1.9748 | 137.437 | 0.45812 | 0.45812 | 0.45812 | 0.45812 | 4.4643e-10 | 4.4643e-10 | 22.9062 | 22.9062 | 22.9062 | 22.9062 | 1.3744 | 1.3744 | 1.3744 | 1.3744 | 964.4867 | 3.215 | 3.215 | 3.215 | 3.215 | 3.1329e-09 | 3.1329e-09 | 160.7478 | 160.7478 | 160.7478 | 160.7478 | 9.6449 | 9.6449 | 9.6449 | 9.6449
FDAMC-180 | c | 4DRG | DAPjm | Feeder Regulator | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Regulator sensor data request to Feeder Regulator | FeederRegulator_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrVR per ¦ hour | > 99.5% | < 3 sec | 150 | x hour |  | X | X | down |  | x | FDAMC-007 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 150 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 1.5625e-08 | 1.5625e-08 | 7.0139 | 7.0139 | 7.0139 | 7.0139 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 461.2359 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 8.3333e-09 | 8.3333e-09 | 19.2182 | 19.2182 | 19.2182 | 19.2182 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 197.4792 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 5.102e-10 | 5.102e-10 | 8.2283 | 8.2283 | 8.2283 | 8.2283 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 137.437 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 1.1161e-10 | 1.1161e-10 | 5.7265 | 5.7265 | 5.7265 | 5.7265 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 964.4867 | 0.26791 | 0.26791 | 0.26791 | 0.26791 | 7.8322e-10 | 7.8322e-10 | 40.1869 | 40.1869 | 40.1869 | 40.1869 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-181 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator sensor data reply to DAPjm | FeederRegulator_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrVR per ¦ hour | > 99.5% | < 3 sec | 1000 | x hour |  | X | X | up |  | x | FDAMC-010 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 0.75 | 1000 | 4 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 | 0.04676 | 0.04676 | 0.18704 | 0.18704 | 1.0417e-07 | 1.0417e-07 | 46.7596 | 46.7596 | 48.443 | 48.443 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 461.2359 | 0.12812 | 0.12812 | 0.51248 | 0.51248 | 5.5556e-08 | 5.5556e-08 | 128.1211 | 128.1211 | 132.7334 | 132.7334 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 197.4792 | 0.054855 | 0.054855 | 0.21942 | 0.21942 | 3.4014e-09 | 3.4014e-09 | 54.8553 | 54.8553 | 56.8301 | 56.8301 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 137.437 | 0.038177 | 0.038177 | 0.15271 | 0.15271 | 7.4405e-10 | 7.4405e-10 | 38.1769 | 38.1769 | 39.5513 | 39.5513 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 964.4867 | 0.26791 | 0.26791 | 1.0717 | 1.0717 | 5.2215e-09 | 5.2215e-09 | 267.913 | 267.913 | 277.5578 | 277.5578 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-195 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator status change info to DAPjm | FeederRegulator_status_change_alert | alert | 24x7 | 1 per ¦ fdrVR per ¦ hour | > 99.5% | < 3 sec | 100 | x hour |  | X | X | up |  | x | FDAMC-013 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 100 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 1.0417e-08 | 1.0417e-08 | 4.676 | 4.676 | 4.676 | 4.676 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 461.2359 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 5.5556e-09 | 5.5556e-09 | 12.8121 | 12.8121 | 12.8121 | 12.8121 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 197.4792 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 3.4014e-10 | 3.4014e-10 | 5.4855 | 5.4855 | 5.4855 | 5.4855 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 137.437 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 7.4405e-11 | 7.4405e-11 | 3.8177 | 3.8177 | 3.8177 | 3.8177 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 964.4867 | 0.26791 | 0.26791 | 0.26791 | 0.26791 | 5.2215e-10 | 5.2215e-10 | 26.7913 | 26.7913 | 26.7913 | 26.7913 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-209 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator deviation alert to DAPjm | FeederRegulator_deviation_alert | alert | 24x7 | 1 per ¦ fdrVR per ¦ hour | > 99.5% | < 3 sec | 100 | x hour |  | X | X | up |  | x | FDAMC-016 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 100 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 168.3346 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 1.0417e-08 | 1.0417e-08 | 4.676 | 4.676 | 4.676 | 4.676 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 461.2359 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 5.5556e-09 | 5.5556e-09 | 12.8121 | 12.8121 | 12.8121 | 12.8121 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 197.4792 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 3.4014e-10 | 3.4014e-10 | 5.4855 | 5.4855 | 5.4855 | 5.4855 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 137.437 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 7.4405e-11 | 7.4405e-11 | 3.8177 | 3.8177 | 3.8177 | 3.8177 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 964.4867 | 0.26791 | 0.26791 | 0.26791 | 0.26791 | 5.2215e-10 | 5.2215e-10 | 26.7913 | 26.7913 | 26.7913 | 26.7913 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-223 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator alarm condition to DAPjm | FeederRegulator_alarm | alarm | 24x7 | 1 per ¦ fdrVR per ¦ week | > 99.5% | < 3 sec | 100 | week |  | X | X | up |  | x | FDAMC-019 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 100 | 1 | 1.6534e-06 | 0.027778 | [12 empty] | 0 |  | 0 | 168.3346 | 0.00027833 | 4.676 | 0.00027833 | 4.676 | 6.2004e-11 | 1.0417e-06 | 0.027833 | 467.5961 | 0.027833 | 467.5961 | 0.00083499 | 14.0279 | 0.00083499 | 14.0279 | 461.2359 | 0.00076263 | 12.8121 | 0.00076263 | 12.8121 | 3.3069e-11 | 5.5556e-07 | 0.076263 | 1281.2107 | 0.076263 | 1281.2107 | 0.0022879 | 38.4363 | 0.0022879 | 38.4363 | 197.4792 | 0.00032652 | 5.4855 | 0.00032652 | 5.4855 | 2.0246e-12 | 3.4014e-08 | 0.032652 | 548.5533 | 0.032652 | 548.5533 | 0.00097956 | 16.4566 | 0.00097956 | 16.4566 | 137.437 | 0.00022724 | 3.8177 | 0.00022724 | 3.8177 | 4.4289e-13 | 7.4405e-09 | 0.022724 | 381.7695 | 0.022724 | 381.7695 | 0.00068173 | 11.4531 | 0.00068173 | 11.4531 | 964.4867 | 0.0015947 | 26.7913 | 0.0015947 | 26.7913 | 3.108e-12 | 5.2215e-08 | 0.15947 | 2679.1296 | 0.15947 | 2679.1296 | 0.0047842 | 80.3739 | 0.0047842 | 80.3739
FDAMC-237 | c | 4DRG | Feeder Regulator | DAPjm | Field DA Maint - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator failure to DAPjm | FeederRegulator_Operate_failure | alarm | 24x7 | 1 per ¦ fdrVR per ¦ month | > 99.5% | < 3 sec | 100 | month |  | X | X | up |  | x | FDAMC-022 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 100 | 1 | 3.858e-07 | 3.858e-07 | [12 empty] | 0 |  | 0 | 168.3346 | 6.4944e-05 | 6.4944e-05 | 6.4944e-05 | 6.4944e-05 | 1.4468e-11 | 1.4468e-11 | 0.0064944 | 0.0064944 | 0.0064944 | 0.0064944 | 0.00019483 | 0.00019483 | 0.00019483 | 0.00019483 | 461.2359 | 0.00017795 | 0.00017795 | 0.00017795 | 0.00017795 | 7.716e-12 | 7.716e-12 | 0.017795 | 0.017795 | 0.017795 | 0.017795 | 0.00053384 | 0.00053384 | 0.00053384 | 0.00053384 | 197.4792 | 7.6188e-05 | 7.6188e-05 | 7.6188e-05 | 7.6188e-05 | 4.7241e-13 | 4.7241e-13 | 0.0076188 | 0.0076188 | 0.0076188 | 0.0076188 | 0.00022856 | 0.00022856 | 0.00022856 | 0.00022856 | 137.437 | 5.3024e-05 | 5.3024e-05 | 5.3024e-05 | 5.3024e-05 | 1.0334e-13 | 1.0334e-13 | 0.0053024 | 0.0053024 | 0.0053024 | 0.0053024 | 0.00015907 | 0.00015907 | 0.00015907 | 0.00015907 | 964.4867 | 0.0003721 | 0.0003721 | 0.0003721 | 0.0003721 | 7.252e-13 | 7.252e-13 | 0.03721 | 0.03721 | 0.03721 | 0.03721 | 0.0011163 | 0.0011163 | 0.0011163 | 0.0011163
FDAMC-264 | c | 4DCB | DAPjm | Feeder Cap Bank | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank status request to Feeder Cap Bank | FeederCapBank_status_cmd | cmd | 24x7 | 1 per ¦ fdrCB per ¦ 5 min | > 99.5% | < 3 sec | 50 | x min |  | X | X | down |  | x | FDAMC-025 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 0.0033333 | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 | 2.9926 | 2.9926 | 2.9926 | 2.9926 | 3.3333e-07 | 3.3333e-07 | 149.6308 | 149.6308 | 149.6308 | 149.6308 | 8.9778 | 8.9778 | 8.9778 | 8.9778 | 2459.9246 | 8.1997 | 8.1997 | 8.1997 | 8.1997 | 1.7778e-07 | 1.7778e-07 | 409.9874 | 409.9874 | 409.9874 | 409.9874 | 24.5992 | 24.5992 | 24.5992 | 24.5992 | 1053.2224 | 3.5107 | 3.5107 | 3.5107 | 3.5107 | 1.0884e-08 | 1.0884e-08 | 175.5371 | 175.5371 | 175.5371 | 175.5371 | 10.5322 | 10.5322 | 10.5322 | 10.5322 | 732.9974 | 2.4433 | 2.4433 | 2.4433 | 2.4433 | 2.381e-09 | 2.381e-09 | 122.1662 | 122.1662 | 122.1662 | 122.1662 | 7.33 | 7.33 | 7.33 | 7.33 | 5143.9289 | 17.1464 | 17.1464 | 17.1464 | 17.1464 | 1.6709e-08 | 1.6709e-08 | 857.3215 | 857.3215 | 857.3215 | 857.3215 | 51.4393 | 51.4393 | 51.4393 | 51.4393
FDAMC-265 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank status reply to DAPjm | FeederCapBank_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrCB per ¦ 5 min | > 99.5% | < 3 sec | 50 | x min |  | X | X | up |  | x | FDAMC-028 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 0.0033333 | 0.0033333 | [12 empty] | 0 |  | 0 | 897.7846 | 2.9926 | 2.9926 | 2.9926 | 2.9926 | 3.3333e-07 | 3.3333e-07 | 149.6308 | 149.6308 | 149.6308 | 149.6308 | 8.9778 | 8.9778 | 8.9778 | 8.9778 | 2459.9246 | 8.1997 | 8.1997 | 8.1997 | 8.1997 | 1.7778e-07 | 1.7778e-07 | 409.9874 | 409.9874 | 409.9874 | 409.9874 | 24.5992 | 24.5992 | 24.5992 | 24.5992 | 1053.2224 | 3.5107 | 3.5107 | 3.5107 | 3.5107 | 1.0884e-08 | 1.0884e-08 | 175.5371 | 175.5371 | 175.5371 | 175.5371 | 10.5322 | 10.5322 | 10.5322 | 10.5322 | 732.9974 | 2.4433 | 2.4433 | 2.4433 | 2.4433 | 2.381e-09 | 2.381e-09 | 122.1662 | 122.1662 | 122.1662 | 122.1662 | 7.33 | 7.33 | 7.33 | 7.33 | 5143.9289 | 17.1464 | 17.1464 | 17.1464 | 17.1464 | 1.6709e-08 | 1.6709e-08 | 857.3215 | 857.3215 | 857.3215 | 857.3215 | 51.4393 | 51.4393 | 51.4393 | 51.4393
FDAMC-292 | c | 4DCB | DAPjm | Feeder Cap Bank | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank sensor data request to Feeder Cap Bank | FeederCapBank_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrCB per ¦ hour | > 99.5% | < 3 sec | 50 | x hour |  | X | X | down |  | x | FDAMC-031 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 897.7846 | 0.24938 | 0.24938 | 0.24938 | 0.24938 | 2.7778e-08 | 2.7778e-08 | 12.4692 | 12.4692 | 12.4692 | 12.4692 | 0.74815 | 0.74815 | 0.74815 | 0.74815 | 2459.9246 | 0.68331 | 0.68331 | 0.68331 | 0.68331 | 1.4815e-08 | 1.4815e-08 | 34.1656 | 34.1656 | 34.1656 | 34.1656 | 2.0499 | 2.0499 | 2.0499 | 2.0499 | 1053.2224 | 0.29256 | 0.29256 | 0.29256 | 0.29256 | 9.0703e-10 | 9.0703e-10 | 14.6281 | 14.6281 | 14.6281 | 14.6281 | 0.87769 | 0.87769 | 0.87769 | 0.87769 | 732.9974 | 0.20361 | 0.20361 | 0.20361 | 0.20361 | 1.9841e-10 | 1.9841e-10 | 10.1805 | 10.1805 | 10.1805 | 10.1805 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 5143.9289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 1.3924e-09 | 1.3924e-09 | 71.4435 | 71.4435 | 71.4435 | 71.4435 | 4.2866 | 4.2866 | 4.2866 | 4.2866
FDAMC-293 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank sensor data reply to DAPjm | FeederCapBank_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrCB per ¦ hour | > 99.5% | < 3 sec | 100 | x hour |  | X | X | up |  | x | FDAMC-034 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 100 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 897.7846 | 0.24938 | 0.24938 | 0.24938 | 0.24938 | 5.5556e-08 | 5.5556e-08 | 24.9385 | 24.9385 | 24.9385 | 24.9385 | 0.74815 | 0.74815 | 0.74815 | 0.74815 | 2459.9246 | 0.68331 | 0.68331 | 0.68331 | 0.68331 | 2.963e-08 | 2.963e-08 | 68.3312 | 68.3312 | 68.3312 | 68.3312 | 2.0499 | 2.0499 | 2.0499 | 2.0499 | 1053.2224 | 0.29256 | 0.29256 | 0.29256 | 0.29256 | 1.8141e-09 | 1.8141e-09 | 29.2562 | 29.2562 | 29.2562 | 29.2562 | 0.87769 | 0.87769 | 0.87769 | 0.87769 | 732.9974 | 0.20361 | 0.20361 | 0.20361 | 0.20361 | 3.9683e-10 | 3.9683e-10 | 20.361 | 20.361 | 20.361 | 20.361 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 5143.9289 | 1.4289 | 1.4289 | 1.4289 | 1.4289 | 2.7848e-09 | 2.7848e-09 | 142.8869 | 142.8869 | 142.8869 | 142.8869 | 4.2866 | 4.2866 | 4.2866 | 4.2866
FDAMC-307 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank status change info to DAPjm | FeederCapBank_status_change_alert | alert | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-037 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 897.7846 | 0.020782 | 0.020782 | 0.020782 | 0.020782 | 2.3148e-09 | 2.3148e-09 | 1.0391 | 1.0391 | 1.0391 | 1.0391 | 0.062346 | 0.062346 | 0.062346 | 0.062346 | 2459.9246 | 0.056943 | 0.056943 | 0.056943 | 0.056943 | 1.2346e-09 | 1.2346e-09 | 2.8471 | 2.8471 | 2.8471 | 2.8471 | 0.17083 | 0.17083 | 0.17083 | 0.17083 | 1053.2224 | 0.02438 | 0.02438 | 0.02438 | 0.02438 | 7.5586e-11 | 7.5586e-11 | 1.219 | 1.219 | 1.219 | 1.219 | 0.07314 | 0.07314 | 0.07314 | 0.07314 | 732.9974 | 0.016968 | 0.016968 | 0.016968 | 0.016968 | 1.6534e-11 | 1.6534e-11 | 0.84838 | 0.84838 | 0.84838 | 0.84838 | 0.050903 | 0.050903 | 0.050903 | 0.050903 | 5143.9289 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 1.1603e-10 | 1.1603e-10 | 5.9536 | 5.9536 | 5.9536 | 5.9536 | 0.35722 | 0.35722 | 0.35722 | 0.35722
FDAMC-321 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank deviation alert to DAPjm | FeederCapBank_deviation_alert | alert | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-040 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 897.7846 | 0.020782 | 0.020782 | 0.020782 | 0.020782 | 2.3148e-09 | 2.3148e-09 | 1.0391 | 1.0391 | 1.0391 | 1.0391 | 0.062346 | 0.062346 | 0.062346 | 0.062346 | 2459.9246 | 0.056943 | 0.056943 | 0.056943 | 0.056943 | 1.2346e-09 | 1.2346e-09 | 2.8471 | 2.8471 | 2.8471 | 2.8471 | 0.17083 | 0.17083 | 0.17083 | 0.17083 | 1053.2224 | 0.02438 | 0.02438 | 0.02438 | 0.02438 | 7.5586e-11 | 7.5586e-11 | 1.219 | 1.219 | 1.219 | 1.219 | 0.07314 | 0.07314 | 0.07314 | 0.07314 | 732.9974 | 0.016968 | 0.016968 | 0.016968 | 0.016968 | 1.6534e-11 | 1.6534e-11 | 0.84838 | 0.84838 | 0.84838 | 0.84838 | 0.050903 | 0.050903 | 0.050903 | 0.050903 | 5143.9289 | 0.11907 | 0.11907 | 0.11907 | 0.11907 | 1.1603e-10 | 1.1603e-10 | 5.9536 | 5.9536 | 5.9536 | 5.9536 | 0.35722 | 0.35722 | 0.35722 | 0.35722
FDAMC-335 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank alarm condition to DAPjm | FeederCapBank_alarm | alarm | 24x7 | 1 per ¦ fdrCB per ¦ week | > 99.5% | < 3 sec | 50 | week |  | X | X | up |  | x | FDAMC-043 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 897.7846 | 0.0014844 | 0.0014844 | 0.0014844 | 0.0014844 | 1.6534e-10 | 1.6534e-10 | 0.074222 | 0.074222 | 0.074222 | 0.074222 | 0.0044533 | 0.0044533 | 0.0044533 | 0.0044533 | 2459.9246 | 0.0040673 | 0.0040673 | 0.0040673 | 0.0040673 | 8.8183e-11 | 8.8183e-11 | 0.20337 | 0.20337 | 0.20337 | 0.20337 | 0.012202 | 0.012202 | 0.012202 | 0.012202 | 1053.2224 | 0.0017414 | 0.0017414 | 0.0017414 | 0.0017414 | 5.399e-12 | 5.399e-12 | 0.087072 | 0.087072 | 0.087072 | 0.087072 | 0.0052243 | 0.0052243 | 0.0052243 | 0.0052243 | 732.9974 | 0.001212 | 0.001212 | 0.001212 | 0.001212 | 1.181e-12 | 1.181e-12 | 0.060598 | 0.060598 | 0.060598 | 0.060598 | 0.0036359 | 0.0036359 | 0.0036359 | 0.0036359 | 5143.9289 | 0.0085052 | 0.0085052 | 0.0085052 | 0.0085052 | 8.2881e-12 | 8.2881e-12 | 0.42526 | 0.42526 | 0.42526 | 0.42526 | 0.025516 | 0.025516 | 0.025516 | 0.025516
FDAMC-349 | c | 4DCB | Feeder Cap Bank | DAPjm | Field DA Maint - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank failure to DAPjm | FeederCapBank_Operate_failure | alarm | 24x7 | 1 per ¦ fdrCB per ¦ month | > 99.5% | < 3 sec | 50 | month |  | X | X | up |  | x | FDAMC-046 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 | 3.858e-07 | 3.858e-07 | [12 empty] | 0 |  | 0 | 897.7846 | 0.00034637 | 0.00034637 | 0.00034637 | 0.00034637 | 3.858e-11 | 3.858e-11 | 0.017318 | 0.017318 | 0.017318 | 0.017318 | 0.0010391 | 0.0010391 | 0.0010391 | 0.0010391 | 2459.9246 | 0.00094904 | 0.00094904 | 0.00094904 | 0.00094904 | 2.0576e-11 | 2.0576e-11 | 0.047452 | 0.047452 | 0.047452 | 0.047452 | 0.0028471 | 0.0028471 | 0.0028471 | 0.0028471 | 1053.2224 | 0.00040634 | 0.00040634 | 0.00040634 | 0.00040634 | 1.2598e-12 | 1.2598e-12 | 0.020317 | 0.020317 | 0.020317 | 0.020317 | 0.001219 | 0.001219 | 0.001219 | 0.001219 | 732.9974 | 0.00028279 | 0.00028279 | 0.00028279 | 0.00028279 | 2.7557e-13 | 2.7557e-13 | 0.01414 | 0.01414 | 0.01414 | 0.01414 | 0.00084838 | 0.00084838 | 0.00084838 | 0.00084838 | 5143.9289 | 0.0019845 | 0.0019845 | 0.0019845 | 0.0019845 | 1.9339e-12 | 1.9339e-12 | 0.099227 | 0.099227 | 0.099227 | 0.099227 | 0.0059536 | 0.0059536 | 0.0059536 | 0.0059536
FDAMC-376 | c | 4DS | DAPjm | Feeder Sensor | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Sensor status request to Feeder Sensor | FeederSensor_status_cmd | cmd | 24x7 | 1 per ¦ fdrFS per ¦ 5 sec | > 99.5% | < 3 sec | 50 | x sec |  | X | X | down |  | x | FDAMC-049 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 0.2 | 0.2 | [12 empty] | 0 |  | 0 | 1122.2307 | 224.4461 | 224.4461 | 224.4461 | 224.4461 | 2.5e-05 | 2.5e-05 | 11222.3074 | 11222.3074 | 11222.3074 | 11222.3074 | 673.3384 | 673.3384 | 673.3384 | 673.3384 | 3074.9057 | 614.9811 | 614.9811 | 614.9811 | 614.9811 | 1.3333e-05 | 1.3333e-05 | 30749.0569 | 30749.0569 | 30749.0569 | 30749.0569 | 1844.9434 | 1844.9434 | 1844.9434 | 1844.9434 | 1316.5279 | 263.3056 | 263.3056 | 263.3056 | 263.3056 | 8.1633e-07 | 8.1633e-07 | 13165.2795 | 13165.2795 | 13165.2795 | 13165.2795 | 789.9168 | 789.9168 | 789.9168 | 789.9168 | 916.2467 | 183.2493 | 183.2493 | 183.2493 | 183.2493 | 1.7857e-07 | 1.7857e-07 | 9162.4671 | 9162.4671 | 9162.4671 | 9162.4671 | 549.748 | 549.748 | 549.748 | 549.748 | 6429.9111 | 1285.9822 | 1285.9822 | 1285.9822 | 1285.9822 | 1.2532e-06 | 1.2532e-06 | 64299.1109 | 64299.1109 | 64299.1109 | 64299.1109 | 3857.9467 | 3857.9467 | 3857.9467 | 3857.9467
FDAMC-377 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor status reply to DAPjm | FeederSensor_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrFS per ¦ 5 sec | > 99.5% | < 3 sec | 50 | x sec |  | X | X | up |  | x | FDAMC-052 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 0.2 | 0.2 | [12 empty] | 0 |  | 0 | 1122.2307 | 224.4461 | 224.4461 | 224.4461 | 224.4461 | 2.5e-05 | 2.5e-05 | 11222.3074 | 11222.3074 | 11222.3074 | 11222.3074 | 673.3384 | 673.3384 | 673.3384 | 673.3384 | 3074.9057 | 614.9811 | 614.9811 | 614.9811 | 614.9811 | 1.3333e-05 | 1.3333e-05 | 30749.0569 | 30749.0569 | 30749.0569 | 30749.0569 | 1844.9434 | 1844.9434 | 1844.9434 | 1844.9434 | 1316.5279 | 263.3056 | 263.3056 | 263.3056 | 263.3056 | 8.1633e-07 | 8.1633e-07 | 13165.2795 | 13165.2795 | 13165.2795 | 13165.2795 | 789.9168 | 789.9168 | 789.9168 | 789.9168 | 916.2467 | 183.2493 | 183.2493 | 183.2493 | 183.2493 | 1.7857e-07 | 1.7857e-07 | 9162.4671 | 9162.4671 | 9162.4671 | 9162.4671 | 549.748 | 549.748 | 549.748 | 549.748 | 6429.9111 | 1285.9822 | 1285.9822 | 1285.9822 | 1285.9822 | 1.2532e-06 | 1.2532e-06 | 64299.1109 | 64299.1109 | 64299.1109 | 64299.1109 | 3857.9467 | 3857.9467 | 3857.9467 | 3857.9467
FDAMC-404 | c | 4DS | DAPjm | Feeder Sensor | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Sensor data request to Feeder Sensor | FeederSensor_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrFS per ¦ 5 sec | > 99.5% | < 3 sec | 150 | x sec |  | X | X | down |  | x | FDAMC-055 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 150 | 1 | 0.2 | 0.2 | [12 empty] | 0 |  | 0 | 1122.2307 | 224.4461 | 224.4461 | 224.4461 | 224.4461 | 7.5e-05 | 7.5e-05 | 33666.9222 | 33666.9222 | 33666.9222 | 33666.9222 | 673.3384 | 673.3384 | 673.3384 | 673.3384 | 3074.9057 | 614.9811 | 614.9811 | 614.9811 | 614.9811 | 4e-05 | 4e-05 | 92247.1707 | 92247.1707 | 92247.1707 | 92247.1707 | 1844.9434 | 1844.9434 | 1844.9434 | 1844.9434 | 1316.5279 | 263.3056 | 263.3056 | 263.3056 | 263.3056 | 2.449e-06 | 2.449e-06 | 39495.8384 | 39495.8384 | 39495.8384 | 39495.8384 | 789.9168 | 789.9168 | 789.9168 | 789.9168 | 916.2467 | 183.2493 | 183.2493 | 183.2493 | 183.2493 | 5.3571e-07 | 5.3571e-07 | 27487.4014 | 27487.4014 | 27487.4014 | 27487.4014 | 549.748 | 549.748 | 549.748 | 549.748 | 6429.9111 | 1285.9822 | 1285.9822 | 1285.9822 | 1285.9822 | 3.7595e-06 | 3.7595e-06 | 192897.3327 | 192897.3327 | 192897.3327 | 192897.3327 | 3857.9467 | 3857.9467 | 3857.9467 | 3857.9467
FDAMC-405 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor data reply to DAPjm | FeederSensor_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrFS per ¦ 5 sec | > 99.5% | < 3 sec | 250 | x sec |  | X | X | up |  | x | FDAMC-058 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 250 | 1 | 0.2 | 0.2 | [12 empty] | 0 |  | 0 | 1122.2307 | 224.4461 | 224.4461 | 224.4461 | 224.4461 | 0.000125 | 0.000125 | 56111.537 | 56111.537 | 56111.537 | 56111.537 | 673.3384 | 673.3384 | 673.3384 | 673.3384 | 3074.9057 | 614.9811 | 614.9811 | 614.9811 | 614.9811 | 6.6667e-05 | 6.6667e-05 | 153745.2846 | 153745.2846 | 153745.2846 | 153745.2846 | 1844.9434 | 1844.9434 | 1844.9434 | 1844.9434 | 1316.5279 | 263.3056 | 263.3056 | 263.3056 | 263.3056 | 4.0816e-06 | 4.0816e-06 | 65826.3974 | 65826.3974 | 65826.3974 | 65826.3974 | 789.9168 | 789.9168 | 789.9168 | 789.9168 | 916.2467 | 183.2493 | 183.2493 | 183.2493 | 183.2493 | 8.9286e-07 | 8.9286e-07 | 45812.3356 | 45812.3356 | 45812.3356 | 45812.3356 | 549.748 | 549.748 | 549.748 | 549.748 | 6429.9111 | 1285.9822 | 1285.9822 | 1285.9822 | 1285.9822 | 6.2658e-06 | 6.2658e-06 | 321495.5546 | 321495.5546 | 321495.5546 | 321495.5546 | 3857.9467 | 3857.9467 | 3857.9467 | 3857.9467
FDAMC-419 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor status change info to DAPjm | FeederSensor_status_change_alert | alert | 24x7 | 1 per ¦ fdrFS per ¦ hour | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-061 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.31173 | 0.31173 | 0.31173 | 0.31173 | 3.4722e-08 | 3.4722e-08 | 15.5865 | 15.5865 | 15.5865 | 15.5865 | 0.93519 | 0.93519 | 0.93519 | 0.93519 | 3074.9057 | 0.85414 | 0.85414 | 0.85414 | 0.85414 | 1.8519e-08 | 1.8519e-08 | 42.707 | 42.707 | 42.707 | 42.707 | 2.5624 | 2.5624 | 2.5624 | 2.5624 | 1316.5279 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 1.1338e-09 | 1.1338e-09 | 18.2851 | 18.2851 | 18.2851 | 18.2851 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 916.2467 | 0.25451 | 0.25451 | 0.25451 | 0.25451 | 2.4802e-10 | 2.4802e-10 | 12.7256 | 12.7256 | 12.7256 | 12.7256 | 0.76354 | 0.76354 | 0.76354 | 0.76354 | 6429.9111 | 1.7861 | 1.7861 | 1.7861 | 1.7861 | 1.7405e-09 | 1.7405e-09 | 89.3043 | 89.3043 | 89.3043 | 89.3043 | 5.3583 | 5.3583 | 5.3583 | 5.3583
FDAMC-433 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor deviation alert to DAPjm | FeederSensor_deviation_alert | alert | 24x7 | 1 per ¦ fdrFS per ¦ hour | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-064 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.31173 | 0.31173 | 0.31173 | 0.31173 | 3.4722e-08 | 3.4722e-08 | 15.5865 | 15.5865 | 15.5865 | 15.5865 | 0.93519 | 0.93519 | 0.93519 | 0.93519 | 3074.9057 | 0.85414 | 0.85414 | 0.85414 | 0.85414 | 1.8519e-08 | 1.8519e-08 | 42.707 | 42.707 | 42.707 | 42.707 | 2.5624 | 2.5624 | 2.5624 | 2.5624 | 1316.5279 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 1.1338e-09 | 1.1338e-09 | 18.2851 | 18.2851 | 18.2851 | 18.2851 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 916.2467 | 0.25451 | 0.25451 | 0.25451 | 0.25451 | 2.4802e-10 | 2.4802e-10 | 12.7256 | 12.7256 | 12.7256 | 12.7256 | 0.76354 | 0.76354 | 0.76354 | 0.76354 | 6429.9111 | 1.7861 | 1.7861 | 1.7861 | 1.7861 | 1.7405e-09 | 1.7405e-09 | 89.3043 | 89.3043 | 89.3043 | 89.3043 | 5.3583 | 5.3583 | 5.3583 | 5.3583
FDAMC-447 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor alarm condition to DAPjm | FeederSensor_alarm | alarm | 24x7 | 1 per ¦ fdrFS per ¦ day | > 99.5% | < 3 sec | 50 | day |  | X | X | up |  | x | FDAMC-067 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.31173 | 0.31173 | 0.31173 | 0.31173 | 3.4722e-08 | 3.4722e-08 | 15.5865 | 15.5865 | 15.5865 | 15.5865 | 0.93519 | 0.93519 | 0.93519 | 0.93519 | 3074.9057 | 0.85414 | 0.85414 | 0.85414 | 0.85414 | 1.8519e-08 | 1.8519e-08 | 42.707 | 42.707 | 42.707 | 42.707 | 2.5624 | 2.5624 | 2.5624 | 2.5624 | 1316.5279 | 0.3657 | 0.3657 | 0.3657 | 0.3657 | 1.1338e-09 | 1.1338e-09 | 18.2851 | 18.2851 | 18.2851 | 18.2851 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 916.2467 | 0.25451 | 0.25451 | 0.25451 | 0.25451 | 2.4802e-10 | 2.4802e-10 | 12.7256 | 12.7256 | 12.7256 | 12.7256 | 0.76354 | 0.76354 | 0.76354 | 0.76354 | 6429.9111 | 1.7861 | 1.7861 | 1.7861 | 1.7861 | 1.7405e-09 | 1.7405e-09 | 89.3043 | 89.3043 | 89.3043 | 89.3043 | 5.3583 | 5.3583 | 5.3583 | 5.3583
FDAMC-474 | c | 4DRC | DAPjm | Feeder Recloser | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Recloser status request to Feeder Recloser | FeederRecloser_status_cmd | cmd | 24x7 | 1 per ¦ fdrRC per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | down |  | x | FDAMC-070 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 673.3384 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 5.2083e-09 | 5.2083e-09 | 2.338 | 2.338 | 2.338 | 2.338 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 1844.9434 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 2.7778e-09 | 2.7778e-09 | 6.4061 | 6.4061 | 6.4061 | 6.4061 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 789.9168 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 1.7007e-10 | 1.7007e-10 | 2.7428 | 2.7428 | 2.7428 | 2.7428 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 549.748 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 3.7202e-11 | 3.7202e-11 | 1.9088 | 1.9088 | 1.9088 | 1.9088 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 3857.9467 | 0.26791 | 0.26791 | 0.26791 | 0.26791 | 2.6107e-10 | 2.6107e-10 | 13.3956 | 13.3956 | 13.3956 | 13.3956 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-475 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser status reply to DAPjm | FeederRecloser_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrRC per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-073 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 673.3384 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 5.2083e-09 | 5.2083e-09 | 2.338 | 2.338 | 2.338 | 2.338 | 0.14028 | 0.14028 | 0.14028 | 0.14028 | 1844.9434 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 2.7778e-09 | 2.7778e-09 | 6.4061 | 6.4061 | 6.4061 | 6.4061 | 0.38436 | 0.38436 | 0.38436 | 0.38436 | 789.9168 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 1.7007e-10 | 1.7007e-10 | 2.7428 | 2.7428 | 2.7428 | 2.7428 | 0.16457 | 0.16457 | 0.16457 | 0.16457 | 549.748 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 3.7202e-11 | 3.7202e-11 | 1.9088 | 1.9088 | 1.9088 | 1.9088 | 0.11453 | 0.11453 | 0.11453 | 0.11453 | 3857.9467 | 0.26791 | 0.26791 | 0.26791 | 0.26791 | 2.6107e-10 | 2.6107e-10 | 13.3956 | 13.3956 | 13.3956 | 13.3956 | 0.80374 | 0.80374 | 0.80374 | 0.80374
FDAMC-502 | c | 4DRC | DAPjm | Feeder Recloser | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Recloser sensor data request to Feeder Recloser | FeederRecloser_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrRC per ¦ 12 hours | > 99.5% | < 3 sec | 100 | x hour |  | X | X | down |  | x | FDAMC-076 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 100 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 673.3384 | 0.015587 | 0.015587 | 0.015587 | 0.015587 | 3.4722e-09 | 3.4722e-09 | 1.5587 | 1.5587 | 1.5587 | 1.5587 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 1844.9434 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 1.8519e-09 | 1.8519e-09 | 4.2707 | 4.2707 | 4.2707 | 4.2707 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 789.9168 | 0.018285 | 0.018285 | 0.018285 | 0.018285 | 1.1338e-10 | 1.1338e-10 | 1.8285 | 1.8285 | 1.8285 | 1.8285 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 549.748 | 0.012726 | 0.012726 | 0.012726 | 0.012726 | 2.4802e-11 | 2.4802e-11 | 1.2726 | 1.2726 | 1.2726 | 1.2726 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 3857.9467 | 0.089304 | 0.089304 | 0.089304 | 0.089304 | 1.7405e-10 | 1.7405e-10 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 0.26791 | 0.26791 | 0.26791 | 0.26791
FDAMC-503 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser sensor data reply to DAPjm | FeederRecloser_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrRC per ¦ 12 hours | > 99.5% | < 3 sec | 100 | x hour |  | X | X | up |  | x | FDAMC-079 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 100 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 673.3384 | 0.015587 | 0.015587 | 0.015587 | 0.015587 | 3.4722e-09 | 3.4722e-09 | 1.5587 | 1.5587 | 1.5587 | 1.5587 | 0.04676 | 0.04676 | 0.04676 | 0.04676 | 1844.9434 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 1.8519e-09 | 1.8519e-09 | 4.2707 | 4.2707 | 4.2707 | 4.2707 | 0.12812 | 0.12812 | 0.12812 | 0.12812 | 789.9168 | 0.018285 | 0.018285 | 0.018285 | 0.018285 | 1.1338e-10 | 1.1338e-10 | 1.8285 | 1.8285 | 1.8285 | 1.8285 | 0.054855 | 0.054855 | 0.054855 | 0.054855 | 549.748 | 0.012726 | 0.012726 | 0.012726 | 0.012726 | 2.4802e-11 | 2.4802e-11 | 1.2726 | 1.2726 | 1.2726 | 1.2726 | 0.038177 | 0.038177 | 0.038177 | 0.038177 | 3857.9467 | 0.089304 | 0.089304 | 0.089304 | 0.089304 | 1.7405e-10 | 1.7405e-10 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 0.26791 | 0.26791 | 0.26791 | 0.26791
FDAMC-517 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser status change info to DAPjm | FeederRecloser_status_change_alert | alert | 24x7 | 1 per ¦ fdrRC per ¦ day | > 99.5% | < 3 sec | 250 | day |  | X | X | up |  | x | FDAMC-082 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 250 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 673.3384 | 0.18704 | 0.18704 | 0.18704 | 0.18704 | 1.0417e-07 | 1.0417e-07 | 46.7596 | 46.7596 | 46.7596 | 46.7596 | 0.56112 | 0.56112 | 0.56112 | 0.56112 | 1844.9434 | 0.51248 | 0.51248 | 0.51248 | 0.51248 | 5.5556e-08 | 5.5556e-08 | 128.1211 | 128.1211 | 128.1211 | 128.1211 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 789.9168 | 0.21942 | 0.21942 | 0.21942 | 0.21942 | 3.4014e-09 | 3.4014e-09 | 54.8553 | 54.8553 | 54.8553 | 54.8553 | 0.65826 | 0.65826 | 0.65826 | 0.65826 | 549.748 | 0.15271 | 0.15271 | 0.15271 | 0.15271 | 7.4405e-10 | 7.4405e-10 | 38.1769 | 38.1769 | 38.1769 | 38.1769 | 0.45812 | 0.45812 | 0.45812 | 0.45812 | 3857.9467 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 5.2215e-09 | 5.2215e-09 | 267.913 | 267.913 | 267.913 | 267.913 | 3.215 | 3.215 | 3.215 | 3.215
FDAMC-531 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser deviation alert to DAPjm | FeederRecloser_deviation_alert | alert | 24x7 | 1 per ¦ fdrRC per ¦ day | > 99.5% | < 3 sec | 50 | day |  | X | X | up |  | x | FDAMC-085 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 673.3384 | 0.18704 | 0.18704 | 0.18704 | 0.18704 | 2.0833e-08 | 2.0833e-08 | 9.3519 | 9.3519 | 9.3519 | 9.3519 | 0.56112 | 0.56112 | 0.56112 | 0.56112 | 1844.9434 | 0.51248 | 0.51248 | 0.51248 | 0.51248 | 1.1111e-08 | 1.1111e-08 | 25.6242 | 25.6242 | 25.6242 | 25.6242 | 1.5375 | 1.5375 | 1.5375 | 1.5375 | 789.9168 | 0.21942 | 0.21942 | 0.21942 | 0.21942 | 6.8027e-10 | 6.8027e-10 | 10.9711 | 10.9711 | 10.9711 | 10.9711 | 0.65826 | 0.65826 | 0.65826 | 0.65826 | 549.748 | 0.15271 | 0.15271 | 0.15271 | 0.15271 | 1.4881e-10 | 1.4881e-10 | 7.6354 | 7.6354 | 7.6354 | 7.6354 | 0.45812 | 0.45812 | 0.45812 | 0.45812 | 3857.9467 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 1.0443e-09 | 1.0443e-09 | 53.5826 | 53.5826 | 53.5826 | 53.5826 | 3.215 | 3.215 | 3.215 | 3.215
FDAMC-545 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser alarm condition to DAPjm | FeederRecloser_alarm | alarm | 24x7 | 1 per ¦ fdrRC per ¦ week | > 99.5% | < 3 sec | 50 | week |  | X | X | up |  | x | FDAMC-088 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 673.3384 | 0.0011133 | 0.0011133 | 0.0011133 | 0.0011133 | 1.2401e-10 | 1.2401e-10 | 0.055666 | 0.055666 | 0.055666 | 0.055666 | 0.00334 | 0.00334 | 0.00334 | 0.00334 | 1844.9434 | 0.0030505 | 0.0030505 | 0.0030505 | 0.0030505 | 6.6138e-11 | 6.6138e-11 | 0.15253 | 0.15253 | 0.15253 | 0.15253 | 0.0091515 | 0.0091515 | 0.0091515 | 0.0091515 | 789.9168 | 0.0013061 | 0.0013061 | 0.0013061 | 0.0013061 | 4.0492e-12 | 4.0492e-12 | 0.065304 | 0.065304 | 0.065304 | 0.065304 | 0.0039182 | 0.0039182 | 0.0039182 | 0.0039182 | 549.748 | 0.00090897 | 0.00090897 | 0.00090897 | 0.00090897 | 8.8577e-13 | 8.8577e-13 | 0.045449 | 0.045449 | 0.045449 | 0.045449 | 0.0027269 | 0.0027269 | 0.0027269 | 0.0027269 | 3857.9467 | 0.0063789 | 0.0063789 | 0.0063789 | 0.0063789 | 6.216e-12 | 6.216e-12 | 0.31894 | 0.31894 | 0.31894 | 0.31894 | 0.019137 | 0.019137 | 0.019137 | 0.019137
FDAMC-559 | c | 4DRC | Feeder Recloser | DAPjm | Field DA Maint - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser failure to DAPjm | FeederRecloser_Operate_failure | alarm | 24x7 | 1 per ¦ fdrRC per ¦ month | > 99.5% | < 3 sec | 50 | month |  | X | X | up |  | x | FDAMC-091 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 | 3.858e-07 | 3.858e-07 | [12 empty] | 0 |  | 0 | 673.3384 | 0.00025978 | 0.00025978 | 0.00025978 | 0.00025978 | 2.8935e-11 | 2.8935e-11 | 0.012989 | 0.012989 | 0.012989 | 0.012989 | 0.00077933 | 0.00077933 | 0.00077933 | 0.00077933 | 1844.9434 | 0.00071178 | 0.00071178 | 0.00071178 | 0.00071178 | 1.5432e-11 | 1.5432e-11 | 0.035589 | 0.035589 | 0.035589 | 0.035589 | 0.0021354 | 0.0021354 | 0.0021354 | 0.0021354 | 789.9168 | 0.00030475 | 0.00030475 | 0.00030475 | 0.00030475 | 9.4482e-13 | 9.4482e-13 | 0.015238 | 0.015238 | 0.015238 | 0.015238 | 0.00091426 | 0.00091426 | 0.00091426 | 0.00091426 | 549.748 | 0.00021209 | 0.00021209 | 0.00021209 | 0.00021209 | 2.0668e-13 | 2.0668e-13 | 0.010605 | 0.010605 | 0.010605 | 0.010605 | 0.00063628 | 0.00063628 | 0.00063628 | 0.00063628 | 3857.9467 | 0.0014884 | 0.0014884 | 0.0014884 | 0.0014884 | 1.4504e-12 | 1.4504e-12 | 0.07442 | 0.07442 | 0.07442 | 0.07442 | 0.0044652 | 0.0044652 | 0.0044652 | 0.0044652
FDAMC-586 | c | 4DSW | DAPjm | Feeder Switch | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Switch status request to Feeder Switch | FeederSwitch_status_cmd | cmd | 24x7 | 1 per ¦ fdrSW per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | down |  | x | FDAMC-094 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 448.8923 | 0.031173 | 0.031173 | 0.031173 | 0.031173 | 3.4722e-09 | 3.4722e-09 | 1.5587 | 1.5587 | 1.5587 | 1.5587 | 0.093519 | 0.093519 | 0.093519 | 0.093519 | 1229.9623 | 0.085414 | 0.085414 | 0.085414 | 0.085414 | 1.8519e-09 | 1.8519e-09 | 4.2707 | 4.2707 | 4.2707 | 4.2707 | 0.25624 | 0.25624 | 0.25624 | 0.25624 | 526.6112 | 0.03657 | 0.03657 | 0.03657 | 0.03657 | 1.1338e-10 | 1.1338e-10 | 1.8285 | 1.8285 | 1.8285 | 1.8285 | 0.10971 | 0.10971 | 0.10971 | 0.10971 | 366.4987 | 0.025451 | 0.025451 | 0.025451 | 0.025451 | 2.4802e-11 | 2.4802e-11 | 1.2726 | 1.2726 | 1.2726 | 1.2726 | 0.076354 | 0.076354 | 0.076354 | 0.076354 | 2571.9644 | 0.17861 | 0.17861 | 0.17861 | 0.17861 | 1.7405e-10 | 1.7405e-10 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 0.53583 | 0.53583 | 0.53583 | 0.53583
FDAMC-587 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch status reply to DAPjm | FeederSwitch_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrSW per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-097 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 448.8923 | 0.031173 | 0.031173 | 0.031173 | 0.031173 | 3.4722e-09 | 3.4722e-09 | 1.5587 | 1.5587 | 1.5587 | 1.5587 | 0.093519 | 0.093519 | 0.093519 | 0.093519 | 1229.9623 | 0.085414 | 0.085414 | 0.085414 | 0.085414 | 1.8519e-09 | 1.8519e-09 | 4.2707 | 4.2707 | 4.2707 | 4.2707 | 0.25624 | 0.25624 | 0.25624 | 0.25624 | 526.6112 | 0.03657 | 0.03657 | 0.03657 | 0.03657 | 1.1338e-10 | 1.1338e-10 | 1.8285 | 1.8285 | 1.8285 | 1.8285 | 0.10971 | 0.10971 | 0.10971 | 0.10971 | 366.4987 | 0.025451 | 0.025451 | 0.025451 | 0.025451 | 2.4802e-11 | 2.4802e-11 | 1.2726 | 1.2726 | 1.2726 | 1.2726 | 0.076354 | 0.076354 | 0.076354 | 0.076354 | 2571.9644 | 0.17861 | 0.17861 | 0.17861 | 0.17861 | 1.7405e-10 | 1.7405e-10 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 0.53583 | 0.53583 | 0.53583 | 0.53583
FDAMC-614 | c | 4DSW | DAPjm | Feeder Switch | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Feeder Switch sensor data request to Feeder Switch | FeederSwitch_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrSW per ¦ 12 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | down |  | x | FDAMC-100 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 448.8923 | 0.010391 | 0.010391 | 0.010391 | 0.010391 | 1.1574e-09 | 1.1574e-09 | 0.51955 | 0.51955 | 0.51955 | 0.51955 | 0.031173 | 0.031173 | 0.031173 | 0.031173 | 1229.9623 | 0.028471 | 0.028471 | 0.028471 | 0.028471 | 6.1728e-10 | 6.1728e-10 | 1.4236 | 1.4236 | 1.4236 | 1.4236 | 0.085414 | 0.085414 | 0.085414 | 0.085414 | 526.6112 | 0.01219 | 0.01219 | 0.01219 | 0.01219 | 3.7793e-11 | 3.7793e-11 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.03657 | 0.03657 | 0.03657 | 0.03657 | 366.4987 | 0.0084838 | 0.0084838 | 0.0084838 | 0.0084838 | 8.2672e-12 | 8.2672e-12 | 0.42419 | 0.42419 | 0.42419 | 0.42419 | 0.025451 | 0.025451 | 0.025451 | 0.025451 | 2571.9644 | 0.059536 | 0.059536 | 0.059536 | 0.059536 | 5.8016e-11 | 5.8016e-11 | 2.9768 | 2.9768 | 2.9768 | 2.9768 | 0.17861 | 0.17861 | 0.17861 | 0.17861
FDAMC-615 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch sensor data reply to DAPjm | FeederSwitch_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrSW per ¦ 12 hours | > 99.5% | < 3 sec | 100 | x hour |  | X | X | up |  | x | FDAMC-103 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 100 | 1 | 2.3148e-05 | 2.3148e-05 | [12 empty] | 0 |  | 0 | 448.8923 | 0.010391 | 0.010391 | 0.010391 | 0.010391 | 2.3148e-09 | 2.3148e-09 | 1.0391 | 1.0391 | 1.0391 | 1.0391 | 0.031173 | 0.031173 | 0.031173 | 0.031173 | 1229.9623 | 0.028471 | 0.028471 | 0.028471 | 0.028471 | 1.2346e-09 | 1.2346e-09 | 2.8471 | 2.8471 | 2.8471 | 2.8471 | 0.085414 | 0.085414 | 0.085414 | 0.085414 | 526.6112 | 0.01219 | 0.01219 | 0.01219 | 0.01219 | 7.5586e-11 | 7.5586e-11 | 1.219 | 1.219 | 1.219 | 1.219 | 0.03657 | 0.03657 | 0.03657 | 0.03657 | 366.4987 | 0.0084838 | 0.0084838 | 0.0084838 | 0.0084838 | 1.6534e-11 | 1.6534e-11 | 0.84838 | 0.84838 | 0.84838 | 0.84838 | 0.025451 | 0.025451 | 0.025451 | 0.025451 | 2571.9644 | 0.059536 | 0.059536 | 0.059536 | 0.059536 | 1.1603e-10 | 1.1603e-10 | 5.9536 | 5.9536 | 5.9536 | 5.9536 | 0.17861 | 0.17861 | 0.17861 | 0.17861
FDAMC-629 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch status change info to DAPjm | FeederSwitch_status_change_alert | alert | 24x7 | 1 per ¦ fdrSW per ¦ day | > 99.5% | < 3 sec | 50 | day |  | X | X | up |  | x | FDAMC-106 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 | 0.12469 | 0.12469 | 0.12469 | 0.12469 | 1.3889e-08 | 1.3889e-08 | 6.2346 | 6.2346 | 6.2346 | 6.2346 | 0.37408 | 0.37408 | 0.37408 | 0.37408 | 1229.9623 | 0.34166 | 0.34166 | 0.34166 | 0.34166 | 7.4074e-09 | 7.4074e-09 | 17.0828 | 17.0828 | 17.0828 | 17.0828 | 1.025 | 1.025 | 1.025 | 1.025 | 526.6112 | 0.14628 | 0.14628 | 0.14628 | 0.14628 | 4.5351e-10 | 4.5351e-10 | 7.314 | 7.314 | 7.314 | 7.314 | 0.43884 | 0.43884 | 0.43884 | 0.43884 | 366.4987 | 0.10181 | 0.10181 | 0.10181 | 0.10181 | 9.9206e-11 | 9.9206e-11 | 5.0903 | 5.0903 | 5.0903 | 5.0903 | 0.30542 | 0.30542 | 0.30542 | 0.30542 | 2571.9644 | 0.71443 | 0.71443 | 0.71443 | 0.71443 | 6.962e-10 | 6.962e-10 | 35.7217 | 35.7217 | 35.7217 | 35.7217 | 2.1433 | 2.1433 | 2.1433 | 2.1433
FDAMC-643 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch deviation alert to DAPjm | FeederSwitch_deviation_alert | alert | 24x7 | 1 per ¦ fdrSW per ¦ day | > 99.5% | < 3 sec | 50 | day |  | X | X | up |  | x | FDAMC-109 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 0.00027778 | 0.00027778 | [12 empty] | 0 |  | 0 | 448.8923 | 0.12469 | 0.12469 | 0.12469 | 0.12469 | 1.3889e-08 | 1.3889e-08 | 6.2346 | 6.2346 | 6.2346 | 6.2346 | 0.37408 | 0.37408 | 0.37408 | 0.37408 | 1229.9623 | 0.34166 | 0.34166 | 0.34166 | 0.34166 | 7.4074e-09 | 7.4074e-09 | 17.0828 | 17.0828 | 17.0828 | 17.0828 | 1.025 | 1.025 | 1.025 | 1.025 | 526.6112 | 0.14628 | 0.14628 | 0.14628 | 0.14628 | 4.5351e-10 | 4.5351e-10 | 7.314 | 7.314 | 7.314 | 7.314 | 0.43884 | 0.43884 | 0.43884 | 0.43884 | 366.4987 | 0.10181 | 0.10181 | 0.10181 | 0.10181 | 9.9206e-11 | 9.9206e-11 | 5.0903 | 5.0903 | 5.0903 | 5.0903 | 0.30542 | 0.30542 | 0.30542 | 0.30542 | 2571.9644 | 0.71443 | 0.71443 | 0.71443 | 0.71443 | 6.962e-10 | 6.962e-10 | 35.7217 | 35.7217 | 35.7217 | 35.7217 | 2.1433 | 2.1433 | 2.1433 | 2.1433
FDAMC-657 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch alarm condition to DAPjm | FeederSwitch_alarm | alarm | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 50 | week |  | X | X | up |  | x | FDAMC-112 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 448.8923 | 0.00074222 | 0.00074222 | 0.00074222 | 0.00074222 | 8.2672e-11 | 8.2672e-11 | 0.037111 | 0.037111 | 0.037111 | 0.037111 | 0.0022266 | 0.0022266 | 0.0022266 | 0.0022266 | 1229.9623 | 0.0020337 | 0.0020337 | 0.0020337 | 0.0020337 | 4.4092e-11 | 4.4092e-11 | 0.10168 | 0.10168 | 0.10168 | 0.10168 | 0.006101 | 0.006101 | 0.006101 | 0.006101 | 526.6112 | 0.00087072 | 0.00087072 | 0.00087072 | 0.00087072 | 2.6995e-12 | 2.6995e-12 | 0.043536 | 0.043536 | 0.043536 | 0.043536 | 0.0026122 | 0.0026122 | 0.0026122 | 0.0026122 | 366.4987 | 0.00060598 | 0.00060598 | 0.00060598 | 0.00060598 | 5.9051e-13 | 5.9051e-13 | 0.030299 | 0.030299 | 0.030299 | 0.030299 | 0.0018179 | 0.0018179 | 0.0018179 | 0.0018179 | 2571.9644 | 0.0042526 | 0.0042526 | 0.0042526 | 0.0042526 | 4.144e-12 | 4.144e-12 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.012758 | 0.012758 | 0.012758 | 0.012758
FDAMC-671 | c | 4DSW | Feeder Switch | DAPjm | Field DA Maint - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch failure to DAPjm | FeederSwitch_Operate_failure | alarm | 24x7 | 1 per ¦ fdrSW per ¦ month | > 99.5% | < 3 sec | 50 | month |  | X | X | up |  | x | FDAMC-115 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 | 3.858e-07 | 3.858e-07 | [12 empty] | 0 |  | 0 | 448.8923 | 0.00017318 | 0.00017318 | 0.00017318 | 0.00017318 | 1.929e-11 | 1.929e-11 | 0.0086592 | 0.0086592 | 0.0086592 | 0.0086592 | 0.00051955 | 0.00051955 | 0.00051955 | 0.00051955 | 1229.9623 | 0.00047452 | 0.00047452 | 0.00047452 | 0.00047452 | 1.0288e-11 | 1.0288e-11 | 0.023726 | 0.023726 | 0.023726 | 0.023726 | 0.0014236 | 0.0014236 | 0.0014236 | 0.0014236 | 526.6112 | 0.00020317 | 0.00020317 | 0.00020317 | 0.00020317 | 6.2988e-13 | 6.2988e-13 | 0.010158 | 0.010158 | 0.010158 | 0.010158 | 0.0006095 | 0.0006095 | 0.0006095 | 0.0006095 | 366.4987 | 0.0001414 | 0.0001414 | 0.0001414 | 0.0001414 | 1.3779e-13 | 1.3779e-13 | 0.0070698 | 0.0070698 | 0.0070698 | 0.0070698 | 0.00042419 | 0.00042419 | 0.00042419 | 0.00042419 | 2571.9644 | 0.00099227 | 0.00099227 | 0.00099227 | 0.00099227 | 9.6694e-13 | 9.6694e-13 | 0.049614 | 0.049614 | 0.049614 | 0.049614 | 0.0029768 | 0.0029768 | 0.0029768 | 0.0029768
FDAMC-698 | c | 4DS | DAPjm | Feeder Sensor | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Fault Detector status request to (Feeder Fault Detector Sensor) Feeder Sensor | FeederFault_Detector_status_cmd | cmd | 24x7 | 1 per ¦ fdrFS per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | down |  | x | FDAMC-118 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.077933 | 0.077933 | 0.077933 | 0.077933 | 8.6806e-09 | 8.6806e-09 | 3.8966 | 3.8966 | 3.8966 | 3.8966 | 0.2338 | 0.2338 | 0.2338 | 0.2338 | 3074.9057 | 0.21354 | 0.21354 | 0.21354 | 0.21354 | 4.6296e-09 | 4.6296e-09 | 10.6768 | 10.6768 | 10.6768 | 10.6768 | 0.64061 | 0.64061 | 0.64061 | 0.64061 | 1316.5279 | 0.091426 | 0.091426 | 0.091426 | 0.091426 | 2.8345e-10 | 2.8345e-10 | 4.5713 | 4.5713 | 4.5713 | 4.5713 | 0.27428 | 0.27428 | 0.27428 | 0.27428 | 916.2467 | 0.063628 | 0.063628 | 0.063628 | 0.063628 | 6.2004e-11 | 6.2004e-11 | 3.1814 | 3.1814 | 3.1814 | 3.1814 | 0.19088 | 0.19088 | 0.19088 | 0.19088 | 6429.9111 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 4.3512e-10 | 4.3512e-10 | 22.3261 | 22.3261 | 22.3261 | 22.3261 | 1.3396 | 1.3396 | 1.3396 | 1.3396
FDAMC-699 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor (Feeder Fault Detector Senso)r may be able to process & forward Fault Detector status reply to DAPjm | FeederFault_Detector_status_resp-data | resp-data | 24x7 | 1 per ¦ fdrFS per ¦ 4 hours | > 99.5% | < 3 sec | 50 | x hour |  | X | X | up |  | x | FDAMC-121 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 6.9444e-05 | 6.9444e-05 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.077933 | 0.077933 | 0.077933 | 0.077933 | 8.6806e-09 | 8.6806e-09 | 3.8966 | 3.8966 | 3.8966 | 3.8966 | 0.2338 | 0.2338 | 0.2338 | 0.2338 | 3074.9057 | 0.21354 | 0.21354 | 0.21354 | 0.21354 | 4.6296e-09 | 4.6296e-09 | 10.6768 | 10.6768 | 10.6768 | 10.6768 | 0.64061 | 0.64061 | 0.64061 | 0.64061 | 1316.5279 | 0.091426 | 0.091426 | 0.091426 | 0.091426 | 2.8345e-10 | 2.8345e-10 | 4.5713 | 4.5713 | 4.5713 | 4.5713 | 0.27428 | 0.27428 | 0.27428 | 0.27428 | 916.2467 | 0.063628 | 0.063628 | 0.063628 | 0.063628 | 6.2004e-11 | 6.2004e-11 | 3.1814 | 3.1814 | 3.1814 | 3.1814 | 0.19088 | 0.19088 | 0.19088 | 0.19088 | 6429.9111 | 0.44652 | 0.44652 | 0.44652 | 0.44652 | 4.3512e-10 | 4.3512e-10 | 22.3261 | 22.3261 | 22.3261 | 22.3261 | 1.3396 | 1.3396 | 1.3396 | 1.3396
FDAMC-726 | c | 4DS | DAPjm | Feeder Sensor | Field DA Maint - Centralized Control | DAPjm may be able to process & forward Fault Detector sensor data request to (Feeder Fault Detector Sensor) Feeder Sensor | FeederFault_Detector_sensor_data_cmd | cmd | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 100 | week |  | X | X | down |  | x | FDAMC-124 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 100 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.0018555 | 0.0018555 | 0.0018555 | 0.0018555 | 4.1336e-10 | 4.1336e-10 | 0.18555 | 0.18555 | 0.18555 | 0.18555 | 0.0055666 | 0.0055666 | 0.0055666 | 0.0055666 | 3074.9057 | 0.0050842 | 0.0050842 | 0.0050842 | 0.0050842 | 2.2046e-10 | 2.2046e-10 | 0.50842 | 0.50842 | 0.50842 | 0.50842 | 0.015253 | 0.015253 | 0.015253 | 0.015253 | 1316.5279 | 0.0021768 | 0.0021768 | 0.0021768 | 0.0021768 | 1.3497e-11 | 1.3497e-11 | 0.21768 | 0.21768 | 0.21768 | 0.21768 | 0.0065304 | 0.0065304 | 0.0065304 | 0.0065304 | 916.2467 | 0.001515 | 0.001515 | 0.001515 | 0.001515 | 2.9526e-12 | 2.9526e-12 | 0.1515 | 0.1515 | 0.1515 | 0.1515 | 0.0045449 | 0.0045449 | 0.0045449 | 0.0045449 | 6429.9111 | 0.010631 | 0.010631 | 0.010631 | 0.010631 | 2.072e-11 | 2.072e-11 | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 0.031894 | 0.031894 | 0.031894 | 0.031894
FDAMC-727 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor (Feeder Fault Detector Sensor) may be able to process & forward Fault Detector sensor data reply to DAPjm | FeederFault_Detector_sensor_data_resp-data | resp-data | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 1000 | week |  | X | X | up |  | x | FDAMC-127 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 0.75 | 1000 | 4 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.0018555 | 0.0018555 | 0.0074222 | 0.0074222 | 4.1336e-09 | 4.1336e-09 | 1.8555 | 1.8555 | 1.9223 | 1.9223 | 0.0055666 | 0.0055666 | 0.0055666 | 0.0055666 | 3074.9057 | 0.0050842 | 0.0050842 | 0.020337 | 0.020337 | 2.2046e-09 | 2.2046e-09 | 5.0842 | 5.0842 | 5.2672 | 5.2672 | 0.015253 | 0.015253 | 0.015253 | 0.015253 | 1316.5279 | 0.0021768 | 0.0021768 | 0.0087072 | 0.0087072 | 1.3497e-10 | 1.3497e-10 | 2.1768 | 2.1768 | 2.2552 | 2.2552 | 0.0065304 | 0.0065304 | 0.0065304 | 0.0065304 | 916.2467 | 0.001515 | 0.001515 | 0.0060598 | 0.0060598 | 2.9526e-11 | 2.9526e-11 | 1.515 | 1.515 | 1.5695 | 1.5695 | 0.0045449 | 0.0045449 | 0.0045449 | 0.0045449 | 6429.9111 | 0.010631 | 0.010631 | 0.042526 | 0.042526 | 2.072e-10 | 2.072e-10 | 10.6315 | 10.6315 | 11.0142 | 11.0142 | 0.031894 | 0.031894 | 0.031894 | 0.031894
FDAMC-741 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor (Feeder Fault Detector Sensor) may be able to process & forward Fault Detector status change info to DAPjm | FeederFault_Detector_status_change_alert | alert | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 1000 | week |  | X | X | up |  | x | FDAMC-130 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 0.75 | 1000 | 4 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.0018555 | 0.0018555 | 0.0074222 | 0.0074222 | 4.1336e-09 | 4.1336e-09 | 1.8555 | 1.8555 | 1.9223 | 1.9223 | 0.0055666 | 0.0055666 | 0.0055666 | 0.0055666 | 3074.9057 | 0.0050842 | 0.0050842 | 0.020337 | 0.020337 | 2.2046e-09 | 2.2046e-09 | 5.0842 | 5.0842 | 5.2672 | 5.2672 | 0.015253 | 0.015253 | 0.015253 | 0.015253 | 1316.5279 | 0.0021768 | 0.0021768 | 0.0087072 | 0.0087072 | 1.3497e-10 | 1.3497e-10 | 2.1768 | 2.1768 | 2.2552 | 2.2552 | 0.0065304 | 0.0065304 | 0.0065304 | 0.0065304 | 916.2467 | 0.001515 | 0.001515 | 0.0060598 | 0.0060598 | 2.9526e-11 | 2.9526e-11 | 1.515 | 1.515 | 1.5695 | 1.5695 | 0.0045449 | 0.0045449 | 0.0045449 | 0.0045449 | 6429.9111 | 0.010631 | 0.010631 | 0.042526 | 0.042526 | 2.072e-10 | 2.072e-10 | 10.6315 | 10.6315 | 11.0142 | 11.0142 | 0.031894 | 0.031894 | 0.031894 | 0.031894
FDAMC-755 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor (Feeder Fault Detector Sensor) may be able to process & forward Fault Detector deviation alert to DAPjm | FeederFault_Detector_deviation_alert | alert | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 50 | week |  | X | X | up |  | x | FDAMC-133 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.0018555 | 0.0018555 | 0.0018555 | 0.0018555 | 2.0668e-10 | 2.0668e-10 | 0.092777 | 0.092777 | 0.092777 | 0.092777 | 0.0055666 | 0.0055666 | 0.0055666 | 0.0055666 | 3074.9057 | 0.0050842 | 0.0050842 | 0.0050842 | 0.0050842 | 1.1023e-10 | 1.1023e-10 | 0.25421 | 0.25421 | 0.25421 | 0.25421 | 0.015253 | 0.015253 | 0.015253 | 0.015253 | 1316.5279 | 0.0021768 | 0.0021768 | 0.0021768 | 0.0021768 | 6.7487e-12 | 6.7487e-12 | 0.10884 | 0.10884 | 0.10884 | 0.10884 | 0.0065304 | 0.0065304 | 0.0065304 | 0.0065304 | 916.2467 | 0.001515 | 0.001515 | 0.001515 | 0.001515 | 1.4763e-12 | 1.4763e-12 | 0.075748 | 0.075748 | 0.075748 | 0.075748 | 0.0045449 | 0.0045449 | 0.0045449 | 0.0045449 | 6429.9111 | 0.010631 | 0.010631 | 0.010631 | 0.010631 | 1.036e-11 | 1.036e-11 | 0.53157 | 0.53157 | 0.53157 | 0.53157 | 0.031894 | 0.031894 | 0.031894 | 0.031894
FDAMC-769 | c | 4DS | Feeder Sensor | DAPjm | Field DA Maint - Centralized Control | Feeder Sensor (Feeder Fault Detector Sensor) may be able to process & forward Fault Detector alarm condition to DAPjm | FeederFault_Detector_alarm | alarm | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 50 | week |  | X | X | up |  | x | FDAMC-136 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 | 1.6534e-06 | 1.6534e-06 | [12 empty] | 0 |  | 0 | 1122.2307 | 0.0018555 | 0.0018555 | 0.0018555 | 0.0018555 | 2.0668e-10 | 2.0668e-10 | 0.092777 | 0.092777 | 0.092777 | 0.092777 | 0.0055666 | 0.0055666 | 0.0055666 | 0.0055666 | 3074.9057 | 0.0050842 | 0.0050842 | 0.0050842 | 0.0050842 | 1.1023e-10 | 1.1023e-10 | 0.25421 | 0.25421 | 0.25421 | 0.25421 | 0.015253 | 0.015253 | 0.015253 | 0.015253 | 1316.5279 | 0.0021768 | 0.0021768 | 0.0021768 | 0.0021768 | 6.7487e-12 | 6.7487e-12 | 0.10884 | 0.10884 | 0.10884 | 0.10884 | 0.0065304 | 0.0065304 | 0.0065304 | 0.0065304 | 916.2467 | 0.001515 | 0.001515 | 0.001515 | 0.001515 | 1.4763e-12 | 1.4763e-12 | 0.075748 | 0.075748 | 0.075748 | 0.075748 | 0.0045449 | 0.0045449 | 0.0045449 | 0.0045449 | 6429.9111 | 0.010631 | 0.010631 | 0.010631 | 0.010631 | 1.036e-11 | 1.036e-11 | 0.53157 | 0.53157 | 0.53157 | 0.53157 | 0.031894 | 0.031894 | 0.031894 | 0.031894
FPU-0006 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_firmware_update_cmd | cmd | 24x7 | 2 per ¦ ElectrMtr per ¦ metrology firmware update per year | > 98% | 15 min - < 4 hr per 1 mtr | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0001 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 14400 | 1.8646 | 2000000 | 7723 |  | 3.858e-07 | 206400 |  | 0.07963 |  | 614.9796 |  | 0.0044137 |  | 159259.2593 |  | 159279.7241 |  | 1146.6667 |  | 1146.6667 | 615700 |  | 0.23754 |  | 1834.5105 |  | 0.0010583 |  | 475077.1605 |  | 475138.2079 |  | 3420.5556 |  | 3420.5556 | 882800 |  | 0.34059 |  | 2630.3489 |  | 0.018878 |  | 681172.8395 |  | 681260.3702 |  | 4904.4444 |  | 4904.4444 | 485900 |  | 0.18746 |  | 1447.7645 |  | 2.3247e-05 |  | 374922.8395 |  | 374971.0171 |  | 2699.4444 |  | 2699.4444 | 107700 |  | 0.041551 |  | 320.8978 |  | 1.6196e-06 |  | 83101.8519 |  | 83112.5304 |  | 598.3333 |  | 598.3333 | 2298500 |  | 0.88677 |  | 6848.5014 |  | 3.4565e-05 |  | 1773533.9506 |  | 1773761.8497 | 0 | 12769.4444 | 0 | 12769.4444
FPU-0012 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send metrology firmware update broadcast request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ metrology firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0007 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 206400 |  | 3.4127e-06 |  | 0.026356 |  | 1.8916e-07 |  | 6.8254 |  | 6.8263 |  | 2.064 |  | 2.064 | 615700 |  | 1.018e-05 |  | 0.078622 |  | 4.5357e-08 |  | 20.3604 |  | 20.3631 |  | 6.157 |  | 6.157 | 882800 |  | 1.4597e-05 |  | 0.11273 |  | 8.0906e-07 |  | 29.1931 |  | 29.1969 |  | 8.828 |  | 8.828 | 485900 |  | 8.0341e-06 |  | 0.062047 |  | 9.9632e-10 |  | 16.0681 |  | 16.0702 |  | 4.859 |  | 4.859 | 107700 |  | 1.7808e-06 |  | 0.013753 |  | 6.9412e-11 |  | 3.5615 |  | 3.562 |  | 1.077 |  | 1.077 | 2298500 |  | 3.8004e-05 |  | 0.29351 |  | 1.4814e-09 |  | 76.0086 |  | 76.0184 | 0 | 22.985 | 0 | 22.985
FPU-0018 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send metrology firmware update multicast request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ metrology firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0013 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 206400 |  | 3.4127e-06 |  | 0.026356 |  | 1.8916e-07 |  | 6.8254 |  | 6.8263 |  | 2.064 |  | 2.064 | 615700 |  | 1.018e-05 |  | 0.078622 |  | 4.5357e-08 |  | 20.3604 |  | 20.3631 |  | 6.157 |  | 6.157 | 882800 |  | 1.4597e-05 |  | 0.11273 |  | 8.0906e-07 |  | 29.1931 |  | 29.1969 |  | 8.828 |  | 8.828 | 485900 |  | 8.0341e-06 |  | 0.062047 |  | 9.9632e-10 |  | 16.0681 |  | 16.0702 |  | 4.859 |  | 4.859 | 107700 |  | 1.7808e-06 |  | 0.013753 |  | 6.9412e-11 |  | 3.5615 |  | 3.562 |  | 1.077 |  | 1.077 | 2298500 |  | 3.8004e-05 |  | 0.29351 |  | 1.4814e-09 |  | 76.0086 |  | 76.0184 | 0 | 22.985 | 0 | 22.985
FPU-0037 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send NIC firmware update broadcast request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ NIC firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0032 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 206400 |  | 3.4127e-06 |  | 0.026356 |  | 1.8916e-07 |  | 6.8254 |  | 6.8263 |  | 2.064 |  | 2.064 | 615700 |  | 1.018e-05 |  | 0.078622 |  | 4.5357e-08 |  | 20.3604 |  | 20.3631 |  | 6.157 |  | 6.157 | 882800 |  | 1.4597e-05 |  | 0.11273 |  | 8.0906e-07 |  | 29.1931 |  | 29.1969 |  | 8.828 |  | 8.828 | 485900 |  | 8.0341e-06 |  | 0.062047 |  | 9.9632e-10 |  | 16.0681 |  | 16.0702 |  | 4.859 |  | 4.859 | 107700 |  | 1.7808e-06 |  | 0.013753 |  | 6.9412e-11 |  | 3.5615 |  | 3.562 |  | 1.077 |  | 1.077 | 2298500 |  | 3.8004e-05 |  | 0.29351 |  | 1.4814e-09 |  | 76.0086 |  | 76.0184 | 0 | 22.985 | 0 | 22.985
FPU-0043 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send NIC firmware update multicast request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ NIC firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0038 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 206400 |  | 3.4127e-06 |  | 0.026356 |  | 1.8916e-07 |  | 6.8254 |  | 6.8263 |  | 2.064 |  | 2.064 | 615700 |  | 1.018e-05 |  | 0.078622 |  | 4.5357e-08 |  | 20.3604 |  | 20.3631 |  | 6.157 |  | 6.157 | 882800 |  | 1.4597e-05 |  | 0.11273 |  | 8.0906e-07 |  | 29.1931 |  | 29.1969 |  | 8.828 |  | 8.828 | 485900 |  | 8.0341e-06 |  | 0.062047 |  | 9.9632e-10 |  | 16.0681 |  | 16.0702 |  | 4.859 |  | 4.859 | 107700 |  | 1.7808e-06 |  | 0.013753 |  | 6.9412e-11 |  | 3.5615 |  | 3.562 |  | 1.077 |  | 1.077 | 2298500 |  | 3.8004e-05 |  | 0.29351 |  | 1.4814e-09 |  | 76.0086 |  | 76.0184 | 0 | 22.985 | 0 | 22.985
FPU-0098 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send metrology program update broadcast request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ metrology program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0093 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 206400 |  | 7.963e-06 |  | 0.0015448 |  | 1.1034e-08 |  | 0.39815 |  | 0.40011 |  | 2.064 |  | 2.064 | 615700 |  | 2.3754e-05 |  | 0.0046082 |  | 2.6458e-09 |  | 1.1877 |  | 1.1935 |  | 6.157 |  | 6.157 | 882800 |  | 3.4059e-05 |  | 0.0066074 |  | 4.7195e-08 |  | 1.7029 |  | 1.7113 |  | 8.828 |  | 8.828 | 485900 |  | 1.8746e-05 |  | 0.0036368 |  | 5.8119e-11 |  | 0.93731 |  | 0.94192 |  | 4.859 |  | 4.859 | 107700 |  | 4.1551e-06 |  | 0.00080609 |  | 4.049e-12 |  | 0.20775 |  | 0.20878 |  | 1.077 |  | 1.077 | 2298500 |  | 8.8677e-05 |  | 0.017203 |  | 8.6413e-11 |  | 4.4338 |  | 4.4556 | 0 | 22.985 | 0 | 22.985
FPU-0104 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send metrology program update multicast request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ metrology program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0099 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 206400 |  | 7.963e-06 |  | 0.0015448 |  | 1.1034e-08 |  | 0.39815 |  | 0.40011 |  | 2.064 |  | 2.064 | 615700 |  | 2.3754e-05 |  | 0.0046082 |  | 2.6458e-09 |  | 1.1877 |  | 1.1935 |  | 6.157 |  | 6.157 | 882800 |  | 3.4059e-05 |  | 0.0066074 |  | 4.7195e-08 |  | 1.7029 |  | 1.7113 |  | 8.828 |  | 8.828 | 485900 |  | 1.8746e-05 |  | 0.0036368 |  | 5.8119e-11 |  | 0.93731 |  | 0.94192 |  | 4.859 |  | 4.859 | 107700 |  | 4.1551e-06 |  | 0.00080609 |  | 4.049e-12 |  | 0.20775 |  | 0.20878 |  | 1.077 |  | 1.077 | 2298500 |  | 8.8677e-05 |  | 0.017203 |  | 8.6413e-11 |  | 4.4338 |  | 4.4556 | 0 | 22.985 | 0 | 22.985
FPU-0123 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send NIC program update broadcast request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ NIC program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0118 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 206400 |  | 7.963e-06 |  | 0.0015448 |  | 1.1034e-08 |  | 0.39815 |  | 0.40011 |  | 2.064 |  | 2.064 | 615700 |  | 2.3754e-05 |  | 0.0046082 |  | 2.6458e-09 |  | 1.1877 |  | 1.1935 |  | 6.157 |  | 6.157 | 882800 |  | 3.4059e-05 |  | 0.0066074 |  | 4.7195e-08 |  | 1.7029 |  | 1.7113 |  | 8.828 |  | 8.828 | 485900 |  | 1.8746e-05 |  | 0.0036368 |  | 5.8119e-11 |  | 0.93731 |  | 0.94192 |  | 4.859 |  | 4.859 | 107700 |  | 4.1551e-06 |  | 0.00080609 |  | 4.049e-12 |  | 0.20775 |  | 0.20878 |  | 1.077 |  | 1.077 | 2298500 |  | 8.8677e-05 |  | 0.017203 |  | 8.6413e-11 |  | 4.4338 |  | 4.4556 | 0 | 22.985 | 0 | 22.985
FPU-0129 | c | 1D | DAPjm | 2-Way Meter - Electr | Firmware / Program Update | DAPjm may be able to process & send NIC program update multicast request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-ElectrMtr per ¦ NIC program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0124 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 206400 |  | 7.963e-06 |  | 0.0015448 |  | 1.1034e-08 |  | 0.39815 |  | 0.40011 |  | 2.064 |  | 2.064 | 615700 |  | 2.3754e-05 |  | 0.0046082 |  | 2.6458e-09 |  | 1.1877 |  | 1.1935 |  | 6.157 |  | 6.157 | 882800 |  | 3.4059e-05 |  | 0.0066074 |  | 4.7195e-08 |  | 1.7029 |  | 1.7113 |  | 8.828 |  | 8.828 | 485900 |  | 1.8746e-05 |  | 0.0036368 |  | 5.8119e-11 |  | 0.93731 |  | 0.94192 |  | 4.859 |  | 4.859 | 107700 |  | 4.1551e-06 |  | 0.00080609 |  | 4.049e-12 |  | 0.20775 |  | 0.20878 |  | 1.077 |  | 1.077 | 2298500 |  | 8.8677e-05 |  | 0.017203 |  | 8.6413e-11 |  | 4.4338 |  | 4.4556 | 0 | 22.985 | 0 | 22.985
FPU-0150 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 402.5321 |  | 0.002889 |  | 104242.4242 |  | 104255.8194 |  | 23.4545 |  | 23.4545 | 3078.5 |  | 0.07774 |  | 600.3852 |  | 0.00034636 |  | 155479.798 |  | 155499.7771 |  | 34.983 |  | 34.983 | 4414 |  | 0.11146 |  | 860.8415 |  | 0.0061783 |  | 222929.2929 |  | 222957.9393 |  | 50.1591 |  | 50.1591 | 2429.5 |  | 0.061351 |  | 473.8139 |  | 7.6083e-06 |  | 122702.0202 |  | 122717.7874 |  | 27.608 |  | 27.608 | 1077 |  | 0.027197 |  | 210.0422 |  | 1.0601e-06 |  | 54393.9394 |  | 54400.929 |  | 12.2386 |  | 12.2386 | 13063 |  | 0.32987 |  | 2547.6149 |  | 1.2858e-05 |  | 659747.4747 |  | 659832.2523 | 0 | 148.4432 | 0 | 148.4432
FPU-0150 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 402.5321 |  | 0.002889 |  | 104242.4242 |  | 104255.8194 |  | 23.4545 |  | 23.4545 | 3078.5 |  | 0.07774 |  | 600.3852 |  | 0.00034636 |  | 155479.798 |  | 155499.7771 |  | 34.983 |  | 34.983 | 4414 |  | 0.11146 |  | 860.8415 |  | 0.0061783 |  | 222929.2929 |  | 222957.9393 |  | 50.1591 |  | 50.1591 | 2429.5 |  | 0.061351 |  | 473.8139 |  | 7.6083e-06 |  | 122702.0202 |  | 122717.7874 |  | 27.608 |  | 27.608 | 1077 |  | 0.027197 |  | 210.0422 |  | 1.0601e-06 |  | 54393.9394 |  | 54400.929 |  | 12.2386 |  | 12.2386 | 13063 |  | 0.32987 |  | 2547.6149 |  | 1.2858e-05 |  | 659747.4747 |  | 659832.2523 | 0 | 148.4432 | 0 | 148.4432
FPU-0153 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends metrology firmware update confirmation message to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0153 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends metrology firmware update confirmation message to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0162 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 402.5321 |  | 0.002889 |  | 104242.4242 |  | 104255.8194 |  | 15.6364 |  | 15.6364 | 3078.5 |  | 0.07774 |  | 600.3852 |  | 0.00034636 |  | 155479.798 |  | 155499.7771 |  | 23.322 |  | 23.322 | 4414 |  | 0.11146 |  | 860.8415 |  | 0.0061783 |  | 222929.2929 |  | 222957.9393 |  | 33.4394 |  | 33.4394 | 2429.5 |  | 0.061351 |  | 473.8139 |  | 7.6083e-06 |  | 122702.0202 |  | 122717.7874 |  | 18.4053 |  | 18.4053 | 1077 |  | 0.027197 |  | 210.0422 |  | 1.0601e-06 |  | 54393.9394 |  | 54400.929 |  | 8.1591 |  | 8.1591 | 13063 |  | 0.32987 |  | 2547.6149 |  | 1.2858e-05 |  | 659747.4747 |  | 659832.2523 | 0 | 98.9621 | 0 | 98.9621
FPU-0162 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 402.5321 |  | 0.002889 |  | 104242.4242 |  | 104255.8194 |  | 15.6364 |  | 15.6364 | 3078.5 |  | 0.07774 |  | 600.3852 |  | 0.00034636 |  | 155479.798 |  | 155499.7771 |  | 23.322 |  | 23.322 | 4414 |  | 0.11146 |  | 860.8415 |  | 0.0061783 |  | 222929.2929 |  | 222957.9393 |  | 33.4394 |  | 33.4394 | 2429.5 |  | 0.061351 |  | 473.8139 |  | 7.6083e-06 |  | 122702.0202 |  | 122717.7874 |  | 18.4053 |  | 18.4053 | 1077 |  | 0.027197 |  | 210.0422 |  | 1.0601e-06 |  | 54393.9394 |  | 54400.929 |  | 8.1591 |  | 8.1591 | 13063 |  | 0.32987 |  | 2547.6149 |  | 1.2858e-05 |  | 659747.4747 |  | 659832.2523 | 0 | 98.9621 | 0 | 98.9621
FPU-0165 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends NIC firmware update confirmation message to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0165 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends NIC firmware update confirmation message to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0176 | c | 6FD | DAPjm | Field Tool | Firmware / Program Update | DAPjm sends ESI firmware update confirmation message to Field Tool | ESI_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ DAPjm-ESI per ¦ ESI update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0175 |  |  | 0.090909 | 1 | ESIInMtr | ESIInMtr | 5 | 5 | 50 | 1 |  | 2.5253e-05 | 206400 |  | 5.2121 |  | 5.2121 |  | 7.2225e-06 |  | 260.6061 |  | 260.6061 |  | 26.0606 |  | 26.0606 | 615700 |  | 15.548 |  | 15.548 |  | 1.7318e-06 |  | 777.399 |  | 777.399 |  | 77.7399 |  | 77.7399 | 882800 |  | 22.2929 |  | 22.2929 |  | 3.0891e-05 |  | 1114.6465 |  | 1114.6465 |  | 111.4646 |  | 111.4646 | 485900 |  | 12.2702 |  | 12.2702 |  | 3.8041e-08 |  | 613.5101 |  | 613.5101 |  | 61.351 |  | 61.351 | 107700 |  | 2.7197 |  | 2.7197 |  | 2.6503e-09 |  | 135.9848 |  | 135.9848 |  | 13.5985 |  | 13.5985 | 2298500 |  | 58.0429 |  | 58.0429 |  | 5.6561e-08 |  | 2902.1465 |  | 2902.1465 | 0 | 290.2146 | 0 | 290.2146
FPU-0178 | c | 5Ba | ESI - In Meter | DAPjm | Firmware / Program Update | ESI - In Meter shall be able to send ESI firmware update confirmation message to DAPjm | ESI_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ DAPjm-ESIInMtr per ¦ ESIInMtr update from Field Tool event | > 98% | < 5 sec | 50 | event | N |  | X | up |  | x | FPU-0178 |  |  | 0.041667 | 1 | ESIInMtr | ESIInMtr | 5 | 5 | 50 | 1 |  | 1.1574e-05 | 206400 |  | 2.3889 |  | 2.3889 |  | 3.3103e-06 |  | 119.4444 |  | 119.4444 |  | 11.9444 |  | 11.9444 | 615700 |  | 7.1262 |  | 7.1262 |  | 7.9375e-07 |  | 356.3079 |  | 356.3079 |  | 35.6308 |  | 35.6308 | 882800 |  | 10.2176 |  | 10.2176 |  | 1.4159e-05 |  | 510.8796 |  | 510.8796 |  | 51.088 |  | 51.088 | 485900 |  | 5.6238 |  | 5.6238 |  | 1.7436e-08 |  | 281.1921 |  | 281.1921 |  | 28.1192 |  | 28.1192 | 107700 |  | 1.2465 |  | 1.2465 |  | 1.2147e-09 |  | 62.3264 |  | 62.3264 |  | 6.2326 |  | 6.2326 | 2298500 |  | 26.603 |  | 26.603 |  | 2.5924e-08 |  | 1330.1505 |  | 1330.1505 | 0 | 133.015 | 0 | 133.015
FPU-0186 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | up |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 10.1115 |  | 7.2225e-05 |  | 2606.0606 |  | 2618.8824 |  | 1.5636 |  | 1.5636 | 3078.5 |  | 0.07774 |  | 15.0815 |  | 8.6591e-06 |  | 3886.9949 |  | 3906.119 |  | 2.3322 |  | 2.3322 | 4414 |  | 0.11146 |  | 21.6241 |  | 0.00015446 |  | 5573.2323 |  | 5600.6526 |  | 3.3439 |  | 3.3439 | 2429.5 |  | 0.061351 |  | 11.9021 |  | 1.9021e-07 |  | 3067.5505 |  | 3082.6429 |  | 1.8405 |  | 1.8405 | 1077 |  | 0.027197 |  | 5.2762 |  | 2.6503e-08 |  | 1359.8485 |  | 1366.5389 |  | 0.81591 |  | 0.81591 | 13063 |  | 0.32987 |  | 63.9955 |  | 3.2145e-07 |  | 16493.6869 |  | 16574.8358 | 0 | 9.8962 | 0 | 9.8962
FPU-0186 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Electr | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | down |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 10.1115 |  | 7.2225e-05 |  | 2606.0606 |  | 2618.8824 |  | 1.5636 |  | 1.5636 | 3078.5 |  | 0.07774 |  | 15.0815 |  | 8.6591e-06 |  | 3886.9949 |  | 3906.119 |  | 2.3322 |  | 2.3322 | 4414 |  | 0.11146 |  | 21.6241 |  | 0.00015446 |  | 5573.2323 |  | 5600.6526 |  | 3.3439 |  | 3.3439 | 2429.5 |  | 0.061351 |  | 11.9021 |  | 1.9021e-07 |  | 3067.5505 |  | 3082.6429 |  | 1.8405 |  | 1.8405 | 1077 |  | 0.027197 |  | 5.2762 |  | 2.6503e-08 |  | 1359.8485 |  | 1366.5389 |  | 0.81591 |  | 0.81591 | 13063 |  | 0.32987 |  | 63.9955 |  | 3.2145e-07 |  | 16493.6869 |  | 16574.8358 | 0 | 9.8962 | 0 | 9.8962
FPU-0189 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends metrology program update confirmation message to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0189 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends metrology program update confirmation message to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0198 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | up |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 10.1115 |  | 7.2225e-05 |  | 2606.0606 |  | 2618.8824 |  | 1.5636 |  | 1.5636 | 3078.5 |  | 0.07774 |  | 15.0815 |  | 8.6591e-06 |  | 3886.9949 |  | 3906.119 |  | 2.3322 |  | 2.3322 | 4414 |  | 0.11146 |  | 21.6241 |  | 0.00015446 |  | 5573.2323 |  | 5600.6526 |  | 3.3439 |  | 3.3439 | 2429.5 |  | 0.061351 |  | 11.9021 |  | 1.9021e-07 |  | 3067.5505 |  | 3082.6429 |  | 1.8405 |  | 1.8405 | 1077 |  | 0.027197 |  | 5.2762 |  | 2.6503e-08 |  | 1359.8485 |  | 1366.5389 |  | 0.81591 |  | 0.81591 | 13063 |  | 0.32987 |  | 63.9955 |  | 3.2145e-07 |  | 16493.6869 |  | 16574.8358 | 0 | 9.8962 | 0 | 9.8962
FPU-0198 | c | 6FMe | Field Tool | 2-Way Meter - Electr | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Electr | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | down |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 10.1115 |  | 7.2225e-05 |  | 2606.0606 |  | 2618.8824 |  | 1.5636 |  | 1.5636 | 3078.5 |  | 0.07774 |  | 15.0815 |  | 8.6591e-06 |  | 3886.9949 |  | 3906.119 |  | 2.3322 |  | 2.3322 | 4414 |  | 0.11146 |  | 21.6241 |  | 0.00015446 |  | 5573.2323 |  | 5600.6526 |  | 3.3439 |  | 3.3439 | 2429.5 |  | 0.061351 |  | 11.9021 |  | 1.9021e-07 |  | 3067.5505 |  | 3082.6429 |  | 1.8405 |  | 1.8405 | 1077 |  | 0.027197 |  | 5.2762 |  | 2.6503e-08 |  | 1359.8485 |  | 1366.5389 |  | 0.81591 |  | 0.81591 | 13063 |  | 0.32987 |  | 63.9955 |  | 3.2145e-07 |  | 16493.6869 |  | 16574.8358 | 0 | 9.8962 | 0 | 9.8962
FPU-0201 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends NIC program update confirmation message to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0201 | c | 6FMe | 2-Way Meter - Electr | Field Tool | Firmware / Program Update | 2-Way Meter - Electr sends NIC program update confirmation message to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ElectrMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | ElectrMtr | ElectrMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 2064 |  | 0.052121 |  | 0.052121 |  | 7.2225e-08 |  | 2.6061 |  | 2.6061 |  | 0.1303 |  | 0.1303 | 3078.5 |  | 0.07774 |  | 0.07774 |  | 8.6591e-09 |  | 3.887 |  | 3.887 |  | 0.19435 |  | 0.19435 | 4414 |  | 0.11146 |  | 0.11146 |  | 1.5446e-07 |  | 5.5732 |  | 5.5732 |  | 0.27866 |  | 0.27866 | 2429.5 |  | 0.061351 |  | 0.061351 |  | 1.9021e-10 |  | 3.0676 |  | 3.0676 |  | 0.15338 |  | 0.15338 | 1077 |  | 0.027197 |  | 0.027197 |  | 2.6503e-11 |  | 1.3598 |  | 1.3598 |  | 0.067992 |  | 0.067992 | 13063 |  | 0.32987 |  | 0.32987 |  | 3.2145e-10 |  | 16.4937 |  | 16.4937 | 0 | 0.82468 | 0 | 0.82468
FPU-0210 | c | 6FD | DAPjm | Field Tool | Firmware / Program Update | DAPjm sends DAPjm firmware update confirmation message to Field Tool | DAP_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ DAPjm per ¦ firmware update event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0209 |  |  | 0.090909 | 1 | DAPjm | DAPjm | 5 | 5 | 50 | 1 |  | 2.5253e-05 | 205 |  | 0.0051768 |  | 0.0051768 |  | 7.1735e-09 |  | 0.25884 |  | 0.25884 |  | 0.025884 |  | 0.025884 | 449 |  | 0.011338 |  | 0.011338 |  | 1.2629e-09 |  | 0.56692 |  | 0.56692 |  | 0.056692 |  | 0.056692 | 2306 |  | 0.058232 |  | 0.058232 |  | 8.0693e-08 |  | 2.9116 |  | 2.9116 |  | 0.29116 |  | 0.29116 | 16127 |  | 0.40725 |  | 0.40725 |  | 1.2626e-09 |  | 20.3624 |  | 20.3624 |  | 2.0362 |  | 2.0362 | 51310 |  | 1.2957 |  | 1.2957 |  | 1.2626e-09 |  | 64.7854 |  | 64.7854 |  | 6.4785 |  | 6.4785 | 70397 |  | 1.7777 |  | 1.7777 |  | 1.7323e-09 |  | 88.8851 |  | 88.8851 | 0 | 8.8885 | 0 | 8.8885
FPU-0218 | c | 6FD | DAPjm | Field Tool | Firmware / Program Update | DAPjm sends DAPjm program update confirmation message to Field Tool | DAP_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ DAPjm per ¦ program update event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0217 |  |  | 0.090909 | 1 | DAPjm | DAPjm | 5 | 5 | 50 | 1 |  | 8.4175e-07 | 205 |  | 0.00017256 |  | 0.00017256 |  | 2.3912e-10 |  | 0.0086279 |  | 0.0086279 |  | 0.00086279 |  | 0.00086279 | 449 |  | 0.00037795 |  | 0.00037795 |  | 4.2098e-11 |  | 0.018897 |  | 0.018897 |  | 0.0018897 |  | 0.0018897 | 2306 |  | 0.0019411 |  | 0.0019411 |  | 2.6898e-09 |  | 0.097054 |  | 0.097054 |  | 0.0097054 |  | 0.0097054 | 16127 |  | 0.013575 |  | 0.013575 |  | 4.2086e-11 |  | 0.67875 |  | 0.67875 |  | 0.067875 |  | 0.067875 | 51310 |  | 0.04319 |  | 0.04319 |  | 4.2088e-11 |  | 2.1595 |  | 2.1595 |  | 0.21595 |  | 0.21595 | 70397 |  | 0.059257 |  | 0.059257 |  | 5.7744e-11 |  | 2.9628 |  | 2.9628 | 0 | 0.29628 | 0 | 0.29628
FPU-0225 | c | 6FD | Field Tool | DAPjm | Firmware / Program Update | Field Tool shall be able to process & send DAPjm firmware update request (without adversely impacting normal operations) to DAPjm | DAP_firmware_update_cmd | cmd | 7AM - 6PM | x per ¦ DAPjm per ¦ year | > 98% | < 5 min | 400k - 750k | year |  |  | X | up |  | x | FPU-0216 |  |  | 0.090909 | 1 | DAPjm | DAPjm | 300 | 0.10359 | 750000 | 2896 |  | 2.5253e-05 | 205 |  | 0.0051768 |  | 14.9919 |  | 0.0001076 |  | 3882.5758 |  | 3882.9071 |  | 1.553 |  | 1.553 | 449 |  | 0.011338 |  | 32.836 |  | 1.8944e-05 |  | 8503.7879 |  | 8504.5135 |  | 3.4015 |  | 3.4015 | 2306 |  | 0.058232 |  | 168.6408 |  | 0.0012104 |  | 43674.2424 |  | 43677.9693 |  | 17.4697 |  | 17.4697 | 16127 |  | 0.40725 |  | 1179.3887 |  | 1.8939e-05 |  | 305435.6061 |  | 305461.6699 |  | 122.1742 |  | 122.1742 | 51310 |  | 1.2957 |  | 3752.3677 |  | 1.8939e-05 |  | 971780.303 |  | 971863.2283 |  | 388.7121 |  | 388.7121 | 70397 |  | 1.7777 |  | 5148.2251 |  | 2.5985e-05 |  | 1333276.5152 |  | 1333390.2881 | 0 | 533.3106 | 0 | 533.3106
FPU-0228 | c | 6FD | Field Tool | DAPjm | Firmware / Program Update | Field Tool shall be able to process & send DAPjm program update request (without adversely impacting normal operations) to DAPjm | DAP_program_update_cmd | cmd | 7AM - 6PM | 2 per ¦ DAPjm per ¦ year | > 98% | < 5 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0227 |  |  | 0.090909 | 1 | DAPjm | DAPjm | 300 | 1.5464 | 50000 | 194 |  | 2.5253e-05 | 205 |  | 0.0051768 |  | 1.0043 |  | 7.1735e-06 |  | 258.8384 |  | 260.1119 |  | 1.553 |  | 1.553 | 449 |  | 0.011338 |  | 2.1996 |  | 1.2629e-06 |  | 566.9192 |  | 569.7084 |  | 3.4015 |  | 3.4015 | 2306 |  | 0.058232 |  | 11.2971 |  | 8.0693e-05 |  | 2911.6162 |  | 2925.9413 |  | 17.4697 |  | 17.4697 | 16127 |  | 0.40725 |  | 79.006 |  | 1.2626e-06 |  | 20362.3737 |  | 20462.5566 |  | 122.1742 |  | 122.1742 | 51310 |  | 1.2957 |  | 251.3672 |  | 1.2626e-06 |  | 64785.3535 |  | 65104.0975 |  | 388.7121 |  | 388.7121 | 70397 |  | 1.7777 |  | 344.8742 |  | 1.7323e-06 |  | 88885.101 |  | 89322.4157 | 0 | 533.3106 | 0 | 533.3106
FPU-0231 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update request (without adversely impacting normal operations) to the 2-Way Meter - Gas | metrology_firmware_update_cmd | cmd | 24x7 | 2 per ¦ GasMtr per ¦ metrology firmware update per year | > 98% | 1 hr - < 12 hr per 1 mtr | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0001 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 43200 | 5.5937 | 2000000 | 7723 |  | 3.858e-07 | 180200 |  | 0.069522 |  | 536.9154 |  | 0.0038535 |  | 139043.2099 |  | 139061.0769 |  | 3003.3333 |  | 3003.3333 | 544600 |  | 0.21011 |  | 1622.6643 |  | 0.00093612 |  | 420216.0494 |  | 420270.0471 |  | 9076.6667 |  | 9076.6667 | 710300 |  | 0.27404 |  | 2116.3761 |  | 0.015189 |  | 548070.9877 |  | 548141.4148 |  | 11838.3333 |  | 11838.3333 | 275800 |  | 0.1064 |  | 821.7606 |  | 1.3195e-05 |  | 212808.642 |  | 212835.9879 |  | 4596.6667 |  | 4596.6667 | 50900 |  | 0.019637 |  | 151.6592 |  | 7.6544e-07 |  | 39274.6914 |  | 39279.7382 |  | 848.3333 |  | 848.3333 | 1761800 |  | 0.67971 |  | 5249.3755 |  | 2.6494e-05 |  | 1359413.5802 |  | 1359588.2649 | 0 | 29363.3333 | 0 | 29363.3333
FPU-0236 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update request (without adversely impacting normal operations) to the 2-Way Meter - Water | metrology_firmware_update_cmd | cmd | 24x7 | 2 per ¦ WaterMtr per ¦ metrology firmware update per year | > 98% | 1 hr - < 12 hr per 1 mtr | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0001 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 43200 | 5.5937 | 2000000 | 7723 |  | 3.858e-07 | 126200 |  | 0.048688 |  | 376.0195 |  | 0.0026987 |  | 97376.5432 |  | 97389.0561 |  | 2103.3333 |  | 2103.3333 | 383600 |  | 0.14799 |  | 1142.9563 |  | 0.00065937 |  | 295987.6543 |  | 296025.6887 |  | 6393.3333 |  | 6393.3333 | 909500 |  | 0.35089 |  | 2709.903 |  | 0.019449 |  | 701774.6914 |  | 701864.8694 |  | 15158.3333 |  | 15158.3333 | 279400 |  | 0.10779 |  | 832.487 |  | 1.3368e-05 |  | 215586.4198 |  | 215614.1226 |  | 4656.6667 |  | 4656.6667 | 25600 |  | 0.0098765 |  | 76.2765 |  | 3.8498e-07 |  | 19753.0864 |  | 19755.6247 |  | 426.6667 |  | 426.6667 | 1724300 |  | 0.66524 |  | 5137.6423 |  | 2.593e-05 |  | 1330478.3951 |  | 1330649.3615 | 0 | 28738.3333 | 0 | 28738.3333
FPU-0239 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | metrology_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ metrology firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0007 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 180200 |  | 2.9795e-06 |  | 0.023011 |  | 1.6515e-07 |  | 5.959 |  | 5.9598 |  | 1.802 |  | 1.802 | 544600 |  | 9.0046e-06 |  | 0.069543 |  | 4.0119e-08 |  | 18.0093 |  | 18.0116 |  | 5.446 |  | 5.446 | 710300 |  | 1.1744e-05 |  | 0.090702 |  | 6.5097e-07 |  | 23.4888 |  | 23.4918 |  | 7.103 |  | 7.103 | 275800 |  | 4.5602e-06 |  | 0.035218 |  | 5.6552e-10 |  | 9.1204 |  | 9.1215 |  | 2.758 |  | 2.758 | 50900 |  | 8.416e-07 |  | 0.0064997 |  | 3.2805e-11 |  | 1.6832 |  | 1.6834 |  | 0.509 |  | 0.509 | 1761800 |  | 2.913e-05 |  | 0.22497 |  | 1.1355e-09 |  | 58.2606 |  | 58.2681 | 0 | 17.618 | 0 | 17.618
FPU-0244 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Water | metrology_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ metrology firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0007 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 126200 |  | 2.0866e-06 |  | 0.016115 |  | 1.1566e-07 |  | 4.1733 |  | 4.1738 |  | 1.262 |  | 1.262 | 383600 |  | 6.3426e-06 |  | 0.048984 |  | 2.8259e-08 |  | 12.6852 |  | 12.6868 |  | 3.836 |  | 3.836 | 909500 |  | 1.5038e-05 |  | 0.11614 |  | 8.3353e-07 |  | 30.0761 |  | 30.0799 |  | 9.095 |  | 9.095 | 279400 |  | 4.6197e-06 |  | 0.035678 |  | 5.729e-10 |  | 9.2394 |  | 9.2406 |  | 2.794 |  | 2.794 | 25600 |  | 4.2328e-07 |  | 0.003269 |  | 1.6499e-11 |  | 0.84656 |  | 0.84667 |  | 0.256 |  | 0.256 | 1724300 |  | 2.851e-05 |  | 0.22018 |  | 1.1113e-09 |  | 57.0205 |  | 57.0278 | 0 | 17.243 | 0 | 17.243
FPU-0247 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | metrology_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ metrology firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0013 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 180200 |  | 2.9795e-06 |  | 0.023011 |  | 1.6515e-07 |  | 5.959 |  | 5.9598 |  | 1.802 |  | 1.802 | 544600 |  | 9.0046e-06 |  | 0.069543 |  | 4.0119e-08 |  | 18.0093 |  | 18.0116 |  | 5.446 |  | 5.446 | 710300 |  | 1.1744e-05 |  | 0.090702 |  | 6.5097e-07 |  | 23.4888 |  | 23.4918 |  | 7.103 |  | 7.103 | 275800 |  | 4.5602e-06 |  | 0.035218 |  | 5.6552e-10 |  | 9.1204 |  | 9.1215 |  | 2.758 |  | 2.758 | 50900 |  | 8.416e-07 |  | 0.0064997 |  | 3.2805e-11 |  | 1.6832 |  | 1.6834 |  | 0.509 |  | 0.509 | 1761800 |  | 2.913e-05 |  | 0.22497 |  | 1.1355e-09 |  | 58.2606 |  | 58.2681 | 0 | 17.618 | 0 | 17.618
FPU-0252 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward metrology firmware update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Water | metrology_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ metrology firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0013 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 126200 |  | 2.0866e-06 |  | 0.016115 |  | 1.1566e-07 |  | 4.1733 |  | 4.1738 |  | 1.262 |  | 1.262 | 383600 |  | 6.3426e-06 |  | 0.048984 |  | 2.8259e-08 |  | 12.6852 |  | 12.6868 |  | 3.836 |  | 3.836 | 909500 |  | 1.5038e-05 |  | 0.11614 |  | 8.3353e-07 |  | 30.0761 |  | 30.0799 |  | 9.095 |  | 9.095 | 279400 |  | 4.6197e-06 |  | 0.035678 |  | 5.729e-10 |  | 9.2394 |  | 9.2406 |  | 2.794 |  | 2.794 | 25600 |  | 4.2328e-07 |  | 0.003269 |  | 1.6499e-11 |  | 0.84656 |  | 0.84667 |  | 0.256 |  | 0.256 | 1724300 |  | 2.851e-05 |  | 0.22018 |  | 1.1113e-09 |  | 57.0205 |  | 57.0278 | 0 | 17.243 | 0 | 17.243
FPU-0271 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward NIC firmware update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | NIC_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ NIC firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0032 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 180200 |  | 2.9795e-06 |  | 0.023011 |  | 1.6515e-07 |  | 5.959 |  | 5.9598 |  | 1.802 |  | 1.802 | 544600 |  | 9.0046e-06 |  | 0.069543 |  | 4.0119e-08 |  | 18.0093 |  | 18.0116 |  | 5.446 |  | 5.446 | 710300 |  | 1.1744e-05 |  | 0.090702 |  | 6.5097e-07 |  | 23.4888 |  | 23.4918 |  | 7.103 |  | 7.103 | 275800 |  | 4.5602e-06 |  | 0.035218 |  | 5.6552e-10 |  | 9.1204 |  | 9.1215 |  | 2.758 |  | 2.758 | 50900 |  | 8.416e-07 |  | 0.0064997 |  | 3.2805e-11 |  | 1.6832 |  | 1.6834 |  | 0.509 |  | 0.509 | 1761800 |  | 2.913e-05 |  | 0.22497 |  | 1.1355e-09 |  | 58.2606 |  | 58.2681 | 0 | 17.618 | 0 | 17.618
FPU-0276 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward NIC firmware update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Water | NIC_firmware_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ NIC firmware update broadcast event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0032 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 126200 |  | 2.0866e-06 |  | 0.016115 |  | 1.1566e-07 |  | 4.1733 |  | 4.1738 |  | 1.262 |  | 1.262 | 383600 |  | 6.3426e-06 |  | 0.048984 |  | 2.8259e-08 |  | 12.6852 |  | 12.6868 |  | 3.836 |  | 3.836 | 909500 |  | 1.5038e-05 |  | 0.11614 |  | 8.3353e-07 |  | 30.0761 |  | 30.0799 |  | 9.095 |  | 9.095 | 279400 |  | 4.6197e-06 |  | 0.035678 |  | 5.729e-10 |  | 9.2394 |  | 9.2406 |  | 2.794 |  | 2.794 | 25600 |  | 4.2328e-07 |  | 0.003269 |  | 1.6499e-11 |  | 0.84656 |  | 0.84667 |  | 0.256 |  | 0.256 | 1724300 |  | 2.851e-05 |  | 0.22018 |  | 1.1113e-09 |  | 57.0205 |  | 57.0278 | 0 | 17.243 | 0 | 17.243
FPU-0279 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward NIC firmware update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | NIC_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ NIC firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0038 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 180200 |  | 2.9795e-06 |  | 0.023011 |  | 1.6515e-07 |  | 5.959 |  | 5.9598 |  | 1.802 |  | 1.802 | 544600 |  | 9.0046e-06 |  | 0.069543 |  | 4.0119e-08 |  | 18.0093 |  | 18.0116 |  | 5.446 |  | 5.446 | 710300 |  | 1.1744e-05 |  | 0.090702 |  | 6.5097e-07 |  | 23.4888 |  | 23.4918 |  | 7.103 |  | 7.103 | 275800 |  | 4.5602e-06 |  | 0.035218 |  | 5.6552e-10 |  | 9.1204 |  | 9.1215 |  | 2.758 |  | 2.758 | 50900 |  | 8.416e-07 |  | 0.0064997 |  | 3.2805e-11 |  | 1.6832 |  | 1.6834 |  | 0.509 |  | 0.509 | 1761800 |  | 2.913e-05 |  | 0.22497 |  | 1.1355e-09 |  | 58.2606 |  | 58.2681 | 0 | 17.618 | 0 | 17.618
FPU-0284 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward NIC firmware update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Water | NIC_firmware_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ NIC firmware update per multicast group request event | > 98% | < 7 day | 400k - 2,000k | event | NL |  | X | down |  | x | FPU-0038 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 604800 | 78.3115 | 2000000 | 7723 |  | 1.6534e-11 | 126200 |  | 2.0866e-06 |  | 0.016115 |  | 1.1566e-07 |  | 4.1733 |  | 4.1738 |  | 1.262 |  | 1.262 | 383600 |  | 6.3426e-06 |  | 0.048984 |  | 2.8259e-08 |  | 12.6852 |  | 12.6868 |  | 3.836 |  | 3.836 | 909500 |  | 1.5038e-05 |  | 0.11614 |  | 8.3353e-07 |  | 30.0761 |  | 30.0799 |  | 9.095 |  | 9.095 | 279400 |  | 4.6197e-06 |  | 0.035678 |  | 5.729e-10 |  | 9.2394 |  | 9.2406 |  | 2.794 |  | 2.794 | 25600 |  | 4.2328e-07 |  | 0.003269 |  | 1.6499e-11 |  | 0.84656 |  | 0.84667 |  | 0.256 |  | 0.256 | 1724300 |  | 2.851e-05 |  | 0.22018 |  | 1.1113e-09 |  | 57.0205 |  | 57.0278 | 0 | 17.243 | 0 | 17.243
FPU-0307 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward metrology program update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | metrology_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ metrology program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0093 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 180200 |  | 6.9522e-06 |  | 0.0013487 |  | 9.6337e-09 |  | 0.34761 |  | 0.34932 |  | 1.802 |  | 1.802 | 544600 |  | 2.1011e-05 |  | 0.0040761 |  | 2.3403e-09 |  | 1.0505 |  | 1.0557 |  | 5.446 |  | 5.446 | 710300 |  | 2.7404e-05 |  | 0.0053163 |  | 3.7973e-08 |  | 1.3702 |  | 1.3769 |  | 7.103 |  | 7.103 | 275800 |  | 1.064e-05 |  | 0.0020642 |  | 3.2989e-11 |  | 0.53202 |  | 0.53464 |  | 2.758 |  | 2.758 | 50900 |  | 1.9637e-06 |  | 0.00038096 |  | 1.9136e-12 |  | 0.098187 |  | 0.09867 |  | 0.509 |  | 0.509 | 1761800 |  | 6.7971e-05 |  | 0.013186 |  | 6.6236e-11 |  | 3.3985 |  | 3.4153 | 0 | 17.618 | 0 | 17.618
FPU-0312 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward metrology program update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Water | metrology_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ metrology program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0093 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 126200 |  | 4.8688e-06 |  | 0.00094455 |  | 6.7468e-09 |  | 0.24344 |  | 0.24464 |  | 1.262 |  | 1.262 | 383600 |  | 1.4799e-05 |  | 0.0028711 |  | 1.6484e-09 |  | 0.73997 |  | 0.74361 |  | 3.836 |  | 3.836 | 909500 |  | 3.5089e-05 |  | 0.0068072 |  | 4.8623e-08 |  | 1.7544 |  | 1.7631 |  | 9.095 |  | 9.095 | 279400 |  | 1.0779e-05 |  | 0.0020912 |  | 3.3419e-11 |  | 0.53897 |  | 0.54162 |  | 2.794 |  | 2.794 | 25600 |  | 9.8765e-07 |  | 0.0001916 |  | 9.6244e-13 |  | 0.049383 |  | 0.049626 |  | 0.256 |  | 0.256 | 1724300 |  | 6.6524e-05 |  | 0.012906 |  | 6.4826e-11 |  | 3.3262 |  | 3.3426 | 0 | 17.243 | 0 | 17.243
FPU-0315 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward metrology program update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | metrology_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ metrology program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0099 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 180200 |  | 6.9522e-06 |  | 0.0013487 |  | 9.6337e-09 |  | 0.34761 |  | 0.34932 |  | 1.802 |  | 1.802 | 544600 |  | 2.1011e-05 |  | 0.0040761 |  | 2.3403e-09 |  | 1.0505 |  | 1.0557 |  | 5.446 |  | 5.446 | 710300 |  | 2.7404e-05 |  | 0.0053163 |  | 3.7973e-08 |  | 1.3702 |  | 1.3769 |  | 7.103 |  | 7.103 | 275800 |  | 1.064e-05 |  | 0.0020642 |  | 3.2989e-11 |  | 0.53202 |  | 0.53464 |  | 2.758 |  | 2.758 | 50900 |  | 1.9637e-06 |  | 0.00038096 |  | 1.9136e-12 |  | 0.098187 |  | 0.09867 |  | 0.509 |  | 0.509 | 1761800 |  | 6.7971e-05 |  | 0.013186 |  | 6.6236e-11 |  | 3.3985 |  | 3.4153 | 0 | 17.618 | 0 | 17.618
FPU-0320 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward metrology program update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Water | metrology_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ metrology program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0099 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 126200 |  | 4.8688e-06 |  | 0.00094455 |  | 6.7468e-09 |  | 0.24344 |  | 0.24464 |  | 1.262 |  | 1.262 | 383600 |  | 1.4799e-05 |  | 0.0028711 |  | 1.6484e-09 |  | 0.73997 |  | 0.74361 |  | 3.836 |  | 3.836 | 909500 |  | 3.5089e-05 |  | 0.0068072 |  | 4.8623e-08 |  | 1.7544 |  | 1.7631 |  | 9.095 |  | 9.095 | 279400 |  | 1.0779e-05 |  | 0.0020912 |  | 3.3419e-11 |  | 0.53897 |  | 0.54162 |  | 2.794 |  | 2.794 | 25600 |  | 9.8765e-07 |  | 0.0001916 |  | 9.6244e-13 |  | 0.049383 |  | 0.049626 |  | 0.256 |  | 0.256 | 1724300 |  | 6.6524e-05 |  | 0.012906 |  | 6.4826e-11 |  | 3.3262 |  | 3.3426 | 0 | 17.243 | 0 | 17.243
FPU-0339 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward NIC program update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | NIC_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ NIC program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0118 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 180200 |  | 6.9522e-06 |  | 0.0013487 |  | 9.6337e-09 |  | 0.34761 |  | 0.34932 |  | 1.802 |  | 1.802 | 544600 |  | 2.1011e-05 |  | 0.0040761 |  | 2.3403e-09 |  | 1.0505 |  | 1.0557 |  | 5.446 |  | 5.446 | 710300 |  | 2.7404e-05 |  | 0.0053163 |  | 3.7973e-08 |  | 1.3702 |  | 1.3769 |  | 7.103 |  | 7.103 | 275800 |  | 1.064e-05 |  | 0.0020642 |  | 3.2989e-11 |  | 0.53202 |  | 0.53464 |  | 2.758 |  | 2.758 | 50900 |  | 1.9637e-06 |  | 0.00038096 |  | 1.9136e-12 |  | 0.098187 |  | 0.09867 |  | 0.509 |  | 0.509 | 1761800 |  | 6.7971e-05 |  | 0.013186 |  | 6.6236e-11 |  | 3.3985 |  | 3.4153 | 0 | 17.618 | 0 | 17.618
FPU-0344 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward NIC program update broadcast request (without adversely impacting normal operations) to the 2-Way Meter - Water | NIC_program_update_broadcast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ NIC program update broadcast event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0118 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 126200 |  | 4.8688e-06 |  | 0.00094455 |  | 6.7468e-09 |  | 0.24344 |  | 0.24464 |  | 1.262 |  | 1.262 | 383600 |  | 1.4799e-05 |  | 0.0028711 |  | 1.6484e-09 |  | 0.73997 |  | 0.74361 |  | 3.836 |  | 3.836 | 909500 |  | 3.5089e-05 |  | 0.0068072 |  | 4.8623e-08 |  | 1.7544 |  | 1.7631 |  | 9.095 |  | 9.095 | 279400 |  | 1.0779e-05 |  | 0.0020912 |  | 3.3419e-11 |  | 0.53897 |  | 0.54162 |  | 2.794 |  | 2.794 | 25600 |  | 9.8765e-07 |  | 0.0001916 |  | 9.6244e-13 |  | 0.049383 |  | 0.049626 |  | 0.256 |  | 0.256 | 1724300 |  | 6.6524e-05 |  | 0.012906 |  | 6.4826e-11 |  | 3.3262 |  | 3.3426 | 0 | 17.243 | 0 | 17.243
FPU-0347 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Firmware / Program Update | DAPjm shall be able to process & forward NIC program update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Gas | NIC_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-GasMtr per ¦ NIC program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0124 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 180200 |  | 6.9522e-06 |  | 0.0013487 |  | 9.6337e-09 |  | 0.34761 |  | 0.34932 |  | 1.802 |  | 1.802 | 544600 |  | 2.1011e-05 |  | 0.0040761 |  | 2.3403e-09 |  | 1.0505 |  | 1.0557 |  | 5.446 |  | 5.446 | 710300 |  | 2.7404e-05 |  | 0.0053163 |  | 3.7973e-08 |  | 1.3702 |  | 1.3769 |  | 7.103 |  | 7.103 | 275800 |  | 1.064e-05 |  | 0.0020642 |  | 3.2989e-11 |  | 0.53202 |  | 0.53464 |  | 2.758 |  | 2.758 | 50900 |  | 1.9637e-06 |  | 0.00038096 |  | 1.9136e-12 |  | 0.098187 |  | 0.09867 |  | 0.509 |  | 0.509 | 1761800 |  | 6.7971e-05 |  | 0.013186 |  | 6.6236e-11 |  | 3.3985 |  | 3.4153 | 0 | 17.618 | 0 | 17.618
FPU-0352 | c | 1Dw | DAPjm | 2-Way Meter - Water | Firmware / Program Update | DAPjm shall be able to process & forward NIC program update multicast request (without adversely impacting normal operations) to the 2-Way Meter - Water | NIC_program_update_multicast_cmd | cmd | 24x7 | 1 per ¦ DAPjm-WaterMtr per ¦ NIC program update per multicast group request event | > 98% | < 3 day | 25k - 50k | event | NL |  | X | down |  | x | FPU-0124 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 259200 | 1336.0825 | 50000 | 194 |  | 3.858e-11 | 126200 |  | 4.8688e-06 |  | 0.00094455 |  | 6.7468e-09 |  | 0.24344 |  | 0.24464 |  | 1.262 |  | 1.262 | 383600 |  | 1.4799e-05 |  | 0.0028711 |  | 1.6484e-09 |  | 0.73997 |  | 0.74361 |  | 3.836 |  | 3.836 | 909500 |  | 3.5089e-05 |  | 0.0068072 |  | 4.8623e-08 |  | 1.7544 |  | 1.7631 |  | 9.095 |  | 9.095 | 279400 |  | 1.0779e-05 |  | 0.0020912 |  | 3.3419e-11 |  | 0.53897 |  | 0.54162 |  | 2.794 |  | 2.794 | 25600 |  | 9.8765e-07 |  | 0.0001916 |  | 9.6244e-13 |  | 0.049383 |  | 0.049626 |  | 0.256 |  | 0.256 | 1724300 |  | 6.6524e-05 |  | 0.012906 |  | 6.4826e-11 |  | 3.3262 |  | 3.3426 | 0 | 17.243 | 0 | 17.243
FPU-0364 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Gas | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 351.4355 |  | 0.0025223 |  | 91010.101 |  | 91021.7958 |  | 20.4773 |  | 20.4773 | 2723 |  | 0.068763 |  | 531.0538 |  | 0.00030637 |  | 137525.2525 |  | 137542.9245 |  | 30.9432 |  | 30.9432 | 3551.5 |  | 0.089684 |  | 692.6322 |  | 0.004971 |  | 179368.6869 |  | 179391.7357 |  | 40.358 |  | 40.358 | 1379 |  | 0.034823 |  | 268.9398 |  | 4.3185e-06 |  | 69646.4646 |  | 69655.4142 |  | 15.6705 |  | 15.6705 | 509 |  | 0.012854 |  | 99.2679 |  | 5.0102e-07 |  | 25707.0707 |  | 25710.3741 |  | 5.7841 |  | 5.7841 | 9964.5 |  | 0.25163 |  | 1943.3291 |  | 9.8082e-06 |  | 503257.5758 |  | 503322.2444 | 0 | 113.233 | 0 | 113.233
FPU-0364 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Gas | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 351.4355 |  | 0.0025223 |  | 91010.101 |  | 91021.7958 |  | 20.4773 |  | 20.4773 | 2723 |  | 0.068763 |  | 531.0538 |  | 0.00030637 |  | 137525.2525 |  | 137542.9245 |  | 30.9432 |  | 30.9432 | 3551.5 |  | 0.089684 |  | 692.6322 |  | 0.004971 |  | 179368.6869 |  | 179391.7357 |  | 40.358 |  | 40.358 | 1379 |  | 0.034823 |  | 268.9398 |  | 4.3185e-06 |  | 69646.4646 |  | 69655.4142 |  | 15.6705 |  | 15.6705 | 509 |  | 0.012854 |  | 99.2679 |  | 5.0102e-07 |  | 25707.0707 |  | 25710.3741 |  | 5.7841 |  | 5.7841 | 9964.5 |  | 0.25163 |  | 1943.3291 |  | 9.8082e-06 |  | 503257.5758 |  | 503322.2444 | 0 | 113.233 | 0 | 113.233
FPU-0366 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Water | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 246.1219 |  | 0.0017664 |  | 63737.3737 |  | 63745.564 |  | 14.3409 |  | 14.3409 | 1918 |  | 0.048434 |  | 374.0584 |  | 0.00021579 |  | 96868.6869 |  | 96881.1345 |  | 21.7955 |  | 21.7955 | 4547.5 |  | 0.11484 |  | 886.8773 |  | 0.0063652 |  | 229671.7172 |  | 229701.23 |  | 51.6761 |  | 51.6761 | 1397 |  | 0.035278 |  | 272.4503 |  | 4.3749e-06 |  | 70555.5556 |  | 70564.6219 |  | 15.875 |  | 15.875 | 256 |  | 0.0064646 |  | 49.9265 |  | 2.5198e-07 |  | 12929.2929 |  | 12930.9543 |  | 2.9091 |  | 2.9091 | 9380.5 |  | 0.23688 |  | 1829.4344 |  | 9.2334e-06 |  | 473762.6263 |  | 473823.5048 | 0 | 106.5966 | 0 | 106.5966
FPU-0366 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to 2-Way Meter - Water | metrology_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 15 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0148 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 450 | 0.058268 | 2000000 | 7723 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 246.1219 |  | 0.0017664 |  | 63737.3737 |  | 63745.564 |  | 14.3409 |  | 14.3409 | 1918 |  | 0.048434 |  | 374.0584 |  | 0.00021579 |  | 96868.6869 |  | 96881.1345 |  | 21.7955 |  | 21.7955 | 4547.5 |  | 0.11484 |  | 886.8773 |  | 0.0063652 |  | 229671.7172 |  | 229701.23 |  | 51.6761 |  | 51.6761 | 1397 |  | 0.035278 |  | 272.4503 |  | 4.3749e-06 |  | 70555.5556 |  | 70564.6219 |  | 15.875 |  | 15.875 | 256 |  | 0.0064646 |  | 49.9265 |  | 2.5198e-07 |  | 12929.2929 |  | 12930.9543 |  | 2.9091 |  | 2.9091 | 9380.5 |  | 0.23688 |  | 1829.4344 |  | 9.2334e-06 |  | 473762.6263 |  | 473823.5048 | 0 | 106.5966 | 0 | 106.5966
FPU-0368 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0368 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0370 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0370 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send metrology firmware update request (without adversely impacting normal operations) to Field Tool | metrology_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0151 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0381 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Gas | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 351.4355 |  | 0.0025223 |  | 91010.101 |  | 91021.7958 |  | 13.6515 |  | 13.6515 | 2723 |  | 0.068763 |  | 531.0538 |  | 0.00030637 |  | 137525.2525 |  | 137542.9245 |  | 20.6288 |  | 20.6288 | 3551.5 |  | 0.089684 |  | 692.6322 |  | 0.004971 |  | 179368.6869 |  | 179391.7357 |  | 26.9053 |  | 26.9053 | 1379 |  | 0.034823 |  | 268.9398 |  | 4.3185e-06 |  | 69646.4646 |  | 69655.4142 |  | 10.447 |  | 10.447 | 509 |  | 0.012854 |  | 99.2679 |  | 5.0102e-07 |  | 25707.0707 |  | 25710.3741 |  | 3.8561 |  | 3.8561 | 9964.5 |  | 0.25163 |  | 1943.3291 |  | 9.8082e-06 |  | 503257.5758 |  | 503322.2444 | 0 | 75.4886 | 0 | 75.4886
FPU-0381 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Gas | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 351.4355 |  | 0.0025223 |  | 91010.101 |  | 91021.7958 |  | 13.6515 |  | 13.6515 | 2723 |  | 0.068763 |  | 531.0538 |  | 0.00030637 |  | 137525.2525 |  | 137542.9245 |  | 20.6288 |  | 20.6288 | 3551.5 |  | 0.089684 |  | 692.6322 |  | 0.004971 |  | 179368.6869 |  | 179391.7357 |  | 26.9053 |  | 26.9053 | 1379 |  | 0.034823 |  | 268.9398 |  | 4.3185e-06 |  | 69646.4646 |  | 69655.4142 |  | 10.447 |  | 10.447 | 509 |  | 0.012854 |  | 99.2679 |  | 5.0102e-07 |  | 25707.0707 |  | 25710.3741 |  | 3.8561 |  | 3.8561 | 9964.5 |  | 0.25163 |  | 1943.3291 |  | 9.8082e-06 |  | 503257.5758 |  | 503322.2444 | 0 | 75.4886 | 0 | 75.4886
FPU-0383 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Water | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | up |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 246.1219 |  | 0.0017664 |  | 63737.3737 |  | 63745.564 |  | 9.5606 |  | 9.5606 | 1918 |  | 0.048434 |  | 374.0584 |  | 0.00021579 |  | 96868.6869 |  | 96881.1345 |  | 14.5303 |  | 14.5303 | 4547.5 |  | 0.11484 |  | 886.8773 |  | 0.0063652 |  | 229671.7172 |  | 229701.23 |  | 34.4508 |  | 34.4508 | 1397 |  | 0.035278 |  | 272.4503 |  | 4.3749e-06 |  | 70555.5556 |  | 70564.6219 |  | 10.5833 |  | 10.5833 | 256 |  | 0.0064646 |  | 49.9265 |  | 2.5198e-07 |  | 12929.2929 |  | 12930.9543 |  | 1.9394 |  | 1.9394 | 9380.5 |  | 0.23688 |  | 1829.4344 |  | 9.2334e-06 |  | 473762.6263 |  | 473823.5048 | 0 | 71.0644 | 0 | 71.0644
FPU-0383 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to 2-Way Meter - Water | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 10 min | 400k - 2,000k | event |  |  | X | down |  | x | FPU-0160 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 246.1219 |  | 0.0017664 |  | 63737.3737 |  | 63745.564 |  | 9.5606 |  | 9.5606 | 1918 |  | 0.048434 |  | 374.0584 |  | 0.00021579 |  | 96868.6869 |  | 96881.1345 |  | 14.5303 |  | 14.5303 | 4547.5 |  | 0.11484 |  | 886.8773 |  | 0.0063652 |  | 229671.7172 |  | 229701.23 |  | 34.4508 |  | 34.4508 | 1397 |  | 0.035278 |  | 272.4503 |  | 4.3749e-06 |  | 70555.5556 |  | 70564.6219 |  | 10.5833 |  | 10.5833 | 256 |  | 0.0064646 |  | 49.9265 |  | 2.5198e-07 |  | 12929.2929 |  | 12930.9543 |  | 1.9394 |  | 1.9394 | 9380.5 |  | 0.23688 |  | 1829.4344 |  | 9.2334e-06 |  | 473762.6263 |  | 473823.5048 | 0 | 71.0644 | 0 | 71.0644
FPU-0385 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0385 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0387 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0387 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send NIC firmware update request (without adversely impacting normal operations) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC firmware update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0163 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0397 | c | 5Ba | DAPjm | ESI - In Meter | Firmware / Program Update | DAPjm shall be able to process & send ESI firmware update request (without adversely impacting normal operations) to ESI - In Meter | ESI_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ ESIInMtr per ¦ ESI update from Field Tool event | > 98% | < 5 min | 400k - 750k | event |  |  | X | down |  | x | FPU-0172 |  |  | 0.090909 | 1 | ESIInMtr | ESIInMtr | 300 | 0.10359 | 750000 | 2896 |  | 8.4175e-07 | 206400 |  | 0.17374 |  | 503.1434 |  | 0.0036112 |  | 130303.0303 |  | 130314.1495 |  | 52.1212 |  | 52.1212 | 615700 |  | 0.51827 |  | 1500.8983 |  | 0.00086591 |  | 388699.4949 |  | 388732.664 |  | 155.4798 |  | 155.4798 | 882800 |  | 0.7431 |  | 2152.0108 |  | 0.015446 |  | 557323.2323 |  | 557370.7906 |  | 222.9293 |  | 222.9293 | 485900 |  | 0.40901 |  | 1184.4835 |  | 1.9021e-05 |  | 306755.0505 |  | 306781.2269 |  | 122.702 |  | 122.702 | 107700 |  | 0.090657 |  | 262.5414 |  | 1.3251e-06 |  | 67992.4242 |  | 67998.2263 |  | 27.197 |  | 27.197 | 2298500 |  | 1.9348 |  | 5603.0774 |  | 2.8281e-05 |  | 1451073.2323 |  | 1451197.0572 | 0 | 580.4293 | 0 | 580.4293
FPU-0401 | c | 5Ba | ESI - In Meter | DAPjm | Firmware / Program Update | ESI - In Meter shall be able to process & send ESI firmware update confirmation to DAPjm | ESI_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ ESIInMtr per ¦ ESIInMtr update from Field Tool event | > 98% | < 5 min | 50 | event |  |  | X | up |  | x | FPU-0175 |  |  | 0.090909 | 1 | ESIInMtr | ESIInMtr | 300 | 300 | 50 | 1 |  | 2.5253e-05 | 206400 |  | 5.2121 |  | 5.2121 |  | 7.2225e-06 |  | 260.6061 |  | 260.6061 |  | 1563.6364 |  | 1563.6364 | 615700 |  | 15.548 |  | 15.548 |  | 1.7318e-06 |  | 777.399 |  | 777.399 |  | 4664.3939 |  | 4664.3939 | 882800 |  | 22.2929 |  | 22.2929 |  | 3.0891e-05 |  | 1114.6465 |  | 1114.6465 |  | 6687.8788 |  | 6687.8788 | 485900 |  | 12.2702 |  | 12.2702 |  | 3.8041e-08 |  | 613.5101 |  | 613.5101 |  | 3681.0606 |  | 3681.0606 | 107700 |  | 2.7197 |  | 2.7197 |  | 2.6503e-09 |  | 135.9848 |  | 135.9848 |  | 815.9091 |  | 815.9091 | 2298500 |  | 58.0429 |  | 58.0429 |  | 5.6561e-08 |  | 2902.1465 |  | 2902.1465 | 0 | 17412.8788 | 0 | 17412.8788
FPU-0408 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Gas | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | up |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 8.828 |  | 6.3057e-05 |  | 2275.2525 |  | 2286.4468 |  | 1.3652 |  | 1.3652 | 2723 |  | 0.068763 |  | 13.3399 |  | 7.6591e-06 |  | 3438.1313 |  | 3455.0469 |  | 2.0629 |  | 2.0629 | 3551.5 |  | 0.089684 |  | 17.3988 |  | 0.00012428 |  | 4484.2172 |  | 4506.2795 |  | 2.6905 |  | 2.6905 | 1379 |  | 0.034823 |  | 6.7557 |  | 1.0796e-07 |  | 1741.1616 |  | 1749.7281 |  | 1.0447 |  | 1.0447 | 509 |  | 0.012854 |  | 2.4936 |  | 1.2525e-08 |  | 642.6768 |  | 645.8387 |  | 0.38561 |  | 0.38561 | 9964.5 |  | 0.25163 |  | 48.816 |  | 2.4521e-07 |  | 12581.4394 |  | 12643.3401 | 0 | 7.5489 | 0 | 7.5489
FPU-0408 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Gas | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | down |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 8.828 |  | 6.3057e-05 |  | 2275.2525 |  | 2286.4468 |  | 1.3652 |  | 1.3652 | 2723 |  | 0.068763 |  | 13.3399 |  | 7.6591e-06 |  | 3438.1313 |  | 3455.0469 |  | 2.0629 |  | 2.0629 | 3551.5 |  | 0.089684 |  | 17.3988 |  | 0.00012428 |  | 4484.2172 |  | 4506.2795 |  | 2.6905 |  | 2.6905 | 1379 |  | 0.034823 |  | 6.7557 |  | 1.0796e-07 |  | 1741.1616 |  | 1749.7281 |  | 1.0447 |  | 1.0447 | 509 |  | 0.012854 |  | 2.4936 |  | 1.2525e-08 |  | 642.6768 |  | 645.8387 |  | 0.38561 |  | 0.38561 | 9964.5 |  | 0.25163 |  | 48.816 |  | 2.4521e-07 |  | 12581.4394 |  | 12643.3401 | 0 | 7.5489 | 0 | 7.5489
FPU-0410 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Water | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | up |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 6.1825 |  | 4.4161e-05 |  | 1593.4343 |  | 1601.274 |  | 0.95606 |  | 0.95606 | 1918 |  | 0.048434 |  | 9.3963 |  | 5.3949e-06 |  | 2421.7172 |  | 2433.632 |  | 1.453 |  | 1.453 | 4547.5 |  | 0.11484 |  | 22.2782 |  | 0.00015913 |  | 5741.7929 |  | 5770.0426 |  | 3.4451 |  | 3.4451 | 1397 |  | 0.035278 |  | 6.8439 |  | 1.0937e-07 |  | 1763.8889 |  | 1772.5672 |  | 1.0583 |  | 1.0583 | 256 |  | 0.0064646 |  | 1.2541 |  | 6.2996e-09 |  | 323.2323 |  | 324.8226 |  | 0.19394 |  | 0.19394 | 9380.5 |  | 0.23688 |  | 45.955 |  | 2.3083e-07 |  | 11844.0657 |  | 11902.3385 | 0 | 7.1064 | 0 | 7.1064
FPU-0410 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send metrology program update request (without adversely impacting normal operations) to 2-Way Meter - Water | metrology_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology program update from Field Tool event | > 98% | < 1 min | 25k - 50k | event |  |  | X | down |  | x | FPU-0184 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 6.1825 |  | 4.4161e-05 |  | 1593.4343 |  | 1601.274 |  | 0.95606 |  | 0.95606 | 1918 |  | 0.048434 |  | 9.3963 |  | 5.3949e-06 |  | 2421.7172 |  | 2433.632 |  | 1.453 |  | 1.453 | 4547.5 |  | 0.11484 |  | 22.2782 |  | 0.00015913 |  | 5741.7929 |  | 5770.0426 |  | 3.4451 |  | 3.4451 | 1397 |  | 0.035278 |  | 6.8439 |  | 1.0937e-07 |  | 1763.8889 |  | 1772.5672 |  | 1.0583 |  | 1.0583 | 256 |  | 0.0064646 |  | 1.2541 |  | 6.2996e-09 |  | 323.2323 |  | 324.8226 |  | 0.19394 |  | 0.19394 | 9380.5 |  | 0.23688 |  | 45.955 |  | 2.3083e-07 |  | 11844.0657 |  | 11902.3385 | 0 | 7.1064 | 0 | 7.1064
FPU-0412 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send metrology program update request (without adversely impacting normal operations) to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0412 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send metrology program update request (without adversely impacting normal operations) to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0414 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send metrology program update request (without adversely impacting normal operations) to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0414 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send metrology program update request (without adversely impacting normal operations) to Field Tool | metrology_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ metrology program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0187 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0425 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Gas | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | up |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 8.828 |  | 6.3057e-05 |  | 2275.2525 |  | 2286.4468 |  | 1.3652 |  | 1.3652 | 2723 |  | 0.068763 |  | 13.3399 |  | 7.6591e-06 |  | 3438.1313 |  | 3455.0469 |  | 2.0629 |  | 2.0629 | 3551.5 |  | 0.089684 |  | 17.3988 |  | 0.00012428 |  | 4484.2172 |  | 4506.2795 |  | 2.6905 |  | 2.6905 | 1379 |  | 0.034823 |  | 6.7557 |  | 1.0796e-07 |  | 1741.1616 |  | 1749.7281 |  | 1.0447 |  | 1.0447 | 509 |  | 0.012854 |  | 2.4936 |  | 1.2525e-08 |  | 642.6768 |  | 645.8387 |  | 0.38561 |  | 0.38561 | 9964.5 |  | 0.25163 |  | 48.816 |  | 2.4521e-07 |  | 12581.4394 |  | 12643.3401 | 0 | 7.5489 | 0 | 7.5489
FPU-0425 | c | 6FMg | Field Tool | 2-Way Meter - Gas | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Gas | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | down |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 8.828 |  | 6.3057e-05 |  | 2275.2525 |  | 2286.4468 |  | 1.3652 |  | 1.3652 | 2723 |  | 0.068763 |  | 13.3399 |  | 7.6591e-06 |  | 3438.1313 |  | 3455.0469 |  | 2.0629 |  | 2.0629 | 3551.5 |  | 0.089684 |  | 17.3988 |  | 0.00012428 |  | 4484.2172 |  | 4506.2795 |  | 2.6905 |  | 2.6905 | 1379 |  | 0.034823 |  | 6.7557 |  | 1.0796e-07 |  | 1741.1616 |  | 1749.7281 |  | 1.0447 |  | 1.0447 | 509 |  | 0.012854 |  | 2.4936 |  | 1.2525e-08 |  | 642.6768 |  | 645.8387 |  | 0.38561 |  | 0.38561 | 9964.5 |  | 0.25163 |  | 48.816 |  | 2.4521e-07 |  | 12581.4394 |  | 12643.3401 | 0 | 7.5489 | 0 | 7.5489
FPU-0427 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Water | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | up |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 6.1825 |  | 4.4161e-05 |  | 1593.4343 |  | 1601.274 |  | 0.95606 |  | 0.95606 | 1918 |  | 0.048434 |  | 9.3963 |  | 5.3949e-06 |  | 2421.7172 |  | 2433.632 |  | 1.453 |  | 1.453 | 4547.5 |  | 0.11484 |  | 22.2782 |  | 0.00015913 |  | 5741.7929 |  | 5770.0426 |  | 3.4451 |  | 3.4451 | 1397 |  | 0.035278 |  | 6.8439 |  | 1.0937e-07 |  | 1763.8889 |  | 1772.5672 |  | 1.0583 |  | 1.0583 | 256 |  | 0.0064646 |  | 1.2541 |  | 6.2996e-09 |  | 323.2323 |  | 324.8226 |  | 0.19394 |  | 0.19394 | 9380.5 |  | 0.23688 |  | 45.955 |  | 2.3083e-07 |  | 11844.0657 |  | 11902.3385 | 0 | 7.1064 | 0 | 7.1064
FPU-0427 | c | 6FMw | Field Tool | 2-Way Meter - Water | Firmware / Program Update | Field Tool shall be able to process & send NIC program update request (without adversely impacting normal operations) to 2-Way Meter - Water | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC program update from Field Tool event | > 98% | < 1 min | 1k - 50k | event |  |  | X | down |  | x | FPU-0196 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 30 | 0.15464 | 50000 | 194 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 6.1825 |  | 4.4161e-05 |  | 1593.4343 |  | 1601.274 |  | 0.95606 |  | 0.95606 | 1918 |  | 0.048434 |  | 9.3963 |  | 5.3949e-06 |  | 2421.7172 |  | 2433.632 |  | 1.453 |  | 1.453 | 4547.5 |  | 0.11484 |  | 22.2782 |  | 0.00015913 |  | 5741.7929 |  | 5770.0426 |  | 3.4451 |  | 3.4451 | 1397 |  | 0.035278 |  | 6.8439 |  | 1.0937e-07 |  | 1763.8889 |  | 1772.5672 |  | 1.0583 |  | 1.0583 | 256 |  | 0.0064646 |  | 1.2541 |  | 6.2996e-09 |  | 323.2323 |  | 324.8226 |  | 0.19394 |  | 0.19394 | 9380.5 |  | 0.23688 |  | 45.955 |  | 2.3083e-07 |  | 11844.0657 |  | 11902.3385 | 0 | 7.1064 | 0 | 7.1064
FPU-0429 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send NIC program update request (without adversely impacting normal operations) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0429 | c | 6FMg | 2-Way Meter - Gas | Field Tool | Firmware / Program Update | 2-Way Meter - Gas shall be able to process & send NIC program update request (without adversely impacting normal operations) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ GasMtr per ¦ NIC program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | GasMtr | GasMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1802 |  | 0.045505 |  | 0.045505 |  | 6.3057e-08 |  | 2.2753 |  | 2.2753 |  | 0.11376 |  | 0.11376 | 2723 |  | 0.068763 |  | 0.068763 |  | 7.6591e-09 |  | 3.4381 |  | 3.4381 |  | 0.17191 |  | 0.17191 | 3551.5 |  | 0.089684 |  | 0.089684 |  | 1.2428e-07 |  | 4.4842 |  | 4.4842 |  | 0.22421 |  | 0.22421 | 1379 |  | 0.034823 |  | 0.034823 |  | 1.0796e-10 |  | 1.7412 |  | 1.7412 |  | 0.087058 |  | 0.087058 | 509 |  | 0.012854 |  | 0.012854 |  | 1.2525e-11 |  | 0.64268 |  | 0.64268 |  | 0.032134 |  | 0.032134 | 9964.5 |  | 0.25163 |  | 0.25163 |  | 2.4521e-10 |  | 12.5814 |  | 12.5814 | 0 | 0.62907 | 0 | 0.62907
FPU-0431 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send NIC program update request (without adversely impacting normal operations) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | up |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0431 | c | 6FMw | 2-Way Meter - Water | Field Tool | Firmware / Program Update | 2-Way Meter - Water shall be able to process & send NIC program update request (without adversely impacting normal operations) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ WaterMtr per ¦ NIC program update from Field Tool event | > 98% | < 5 sec | 50 | event |  |  | X | down |  | x | FPU-0199 | D | 0.5 | 0.090909 | 1 | WaterMtr | WaterMtr-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | 1262 |  | 0.031869 |  | 0.031869 |  | 4.4161e-08 |  | 1.5934 |  | 1.5934 |  | 0.079672 |  | 0.079672 | 1918 |  | 0.048434 |  | 0.048434 |  | 5.3949e-09 |  | 2.4217 |  | 2.4217 |  | 0.12109 |  | 0.12109 | 4547.5 |  | 0.11484 |  | 0.11484 |  | 1.5913e-07 |  | 5.7418 |  | 5.7418 |  | 0.28709 |  | 0.28709 | 1397 |  | 0.035278 |  | 0.035278 |  | 1.0937e-10 |  | 1.7639 |  | 1.7639 |  | 0.088194 |  | 0.088194 | 256 |  | 0.0064646 |  | 0.0064646 |  | 6.2996e-12 |  | 0.32323 |  | 0.32323 |  | 0.016162 |  | 0.016162 | 9380.5 |  | 0.23688 |  | 0.23688 |  | 2.3083e-10 |  | 11.8441 |  | 11.8441 | 0 | 0.5922 | 0 | 0.5922
FPU-0474 | c | 4DRG | DAPjm | Feeder Regulator | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Regulator | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrVR per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0001417 |  | 1.0943 |  | 6.3131e-07 |  | 283.3916 |  | 283.428 |  | 2.0404 |  | 2.0404 | 461.2359 |  | 0.00038825 |  | 2.9984 |  | 3.367e-07 |  | 776.4913 |  | 776.5911 |  | 5.5907 |  | 5.5907 | 197.4792 |  | 0.00016623 |  | 1.2838 |  | 2.0614e-08 |  | 332.4566 |  | 332.4993 |  | 2.3937 |  | 2.3937 | 137.437 |  | 0.00011569 |  | 0.89346 |  | 4.5094e-09 |  | 231.3754 |  | 231.4052 |  | 1.6659 |  | 1.6659 | 964.4867 |  | 0.00081186 |  | 6.27 |  | 3.1645e-08 |  | 1623.7149 |  | 1623.9236 | 0 | 11.6907 | 0 | 11.6907
FPU-0475 | c | 4DCB | DAPjm | Feeder Cap Bank | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrCB per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.00075571 |  | 5.8364 |  | 3.367e-06 |  | 1511.4219 |  | 1511.6161 |  | 10.8822 |  | 10.8822 | 2459.9246 |  | 0.0020706 |  | 15.9916 |  | 1.7957e-06 |  | 4141.2871 |  | 4141.8193 |  | 29.8173 |  | 29.8173 | 1053.2224 |  | 0.00088655 |  | 6.8468 |  | 1.0994e-07 |  | 1773.1016 |  | 1773.3295 |  | 12.7663 |  | 12.7663 | 732.9974 |  | 0.000617 |  | 4.7651 |  | 2.405e-08 |  | 1234.0023 |  | 1234.1609 |  | 8.8848 |  | 8.8848 | 5143.9289 |  | 0.0043299 |  | 33.4399 |  | 1.6877e-07 |  | 8659.8129 |  | 8660.9257 | 0 | 62.3507 | 0 | 62.3507
FPU-0476 | c | 4DS | DAPjm | Feeder Sensor | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sensor | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrFS per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.00094464 |  | 7.2954 |  | 4.2088e-06 |  | 1889.2773 |  | 1889.5201 |  | 13.6028 |  | 13.6028 | 3074.9057 |  | 0.0025883 |  | 19.9895 |  | 2.2447e-06 |  | 5176.6089 |  | 5177.2741 |  | 37.2716 |  | 37.2716 | 1316.5279 |  | 0.0011082 |  | 8.5585 |  | 1.3743e-07 |  | 2216.377 |  | 2216.6618 |  | 15.9579 |  | 15.9579 | 916.2467 |  | 0.00077125 |  | 5.9564 |  | 3.0063e-08 |  | 1542.5029 |  | 1542.7011 |  | 11.106 |  | 11.106 | 6429.9111 |  | 0.0054124 |  | 41.7998 |  | 2.1097e-07 |  | 10824.7661 |  | 10826.1571 | 0 | 77.9383 | 0 | 77.9383
FPU-0477 | c | 4DST | DAPjm | Feeder Sectionalizer | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrST per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrST | fdrST | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0478 | c | 4DSW | DAPjm | Feeder Switch | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Switch | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrSW per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00037786 |  | 2.9182 |  | 1.6835e-06 |  | 755.7109 |  | 755.808 |  | 5.4411 |  | 5.4411 | 1229.9623 |  | 0.0010353 |  | 7.9958 |  | 8.9787e-07 |  | 2070.6436 |  | 2070.9096 |  | 14.9086 |  | 14.9086 | 526.6112 |  | 0.00044328 |  | 3.4234 |  | 5.4971e-08 |  | 886.5508 |  | 886.6647 |  | 6.3832 |  | 6.3832 | 366.4987 |  | 0.0003085 |  | 2.3825 |  | 1.2025e-08 |  | 617.0012 |  | 617.0804 |  | 4.4424 |  | 4.4424 | 2571.9644 |  | 0.002165 |  | 16.7199 |  | 8.4387e-08 |  | 4329.9065 |  | 4330.4629 | 0 | 31.1753 | 0 | 31.1753
FPU-0479 | c | 4DRC | DAPjm | Feeder Recloser | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Recloser | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrRC per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.00056678 |  | 4.3773 |  | 2.5253e-06 |  | 1133.5664 |  | 1133.7121 |  | 8.1617 |  | 8.1617 | 1844.9434 |  | 0.001553 |  | 11.9937 |  | 1.3468e-06 |  | 3105.9653 |  | 3106.3645 |  | 22.363 |  | 22.363 | 789.9168 |  | 0.00066491 |  | 5.1351 |  | 8.2457e-08 |  | 1329.8262 |  | 1329.9971 |  | 9.5747 |  | 9.5747 | 549.748 |  | 0.00046275 |  | 3.5738 |  | 1.8038e-08 |  | 925.5017 |  | 925.6207 |  | 6.6636 |  | 6.6636 | 3857.9467 |  | 0.0032474 |  | 25.0799 |  | 1.2658e-07 |  | 6494.8597 |  | 6495.6943 | 0 | 46.763 | 0 | 46.763
FPU-0480 | c | 4DCS | DAPjm | Distr. Cust. Storage | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 0.041413 |  | 319.8316 |  | 0.0022954 |  | 82825.7425 |  | 82836.3856 |  | 596.3453 |  | 596.3453 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.041413 |  | 319.8316 |  | 1.6142e-06 |  | 82825.7425 |  | 82836.3856 | 0 | 596.3453 | 0 | 596.3453
FPU-0481 | c | 4DCG | DAPjm | Distr. Cust. Generation | Firmware / Program Update | DAPjm may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ year | > 99.5% | 20 min - < 4 hr per 1 Distr device | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0469 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 14400 | 1.8646 | 2000000 | 7723 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0512 | c | 4DRG | Feeder Regulator | DAPjm | Firmware / Program Update | Feeder Regulator may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.012753 |  | 0.012753 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.034942 |  | 0.034942 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.014961 |  | 0.014961 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.010412 |  | 0.010412 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.073067 | 0 | 0.073067
FPU-0513 | c | 4DCB | Feeder Cap Bank | DAPjm | Firmware / Program Update | Feeder Cap Bank may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.068014 |  | 0.068014 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.18636 |  | 0.18636 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.07979 |  | 0.07979 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.05553 |  | 0.05553 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.38969 | 0 | 0.38969
FPU-0514 | c | 4DS | Feeder Sensor | DAPjm | Firmware / Program Update | Feeder Sensor may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.085017 |  | 0.085017 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.23295 |  | 0.23295 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.099737 |  | 0.099737 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.069413 |  | 0.069413 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.48711 | 0 | 0.48711
FPU-0515 | c | 4DST | Feeder Sectionalizer | DAPjm | Firmware / Program Update | Feeder Sectionalizer may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrST | fdrST | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0516 | c | 4DSW | Feeder Switch | DAPjm | Firmware / Program Update | Feeder Switch may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.034007 |  | 0.034007 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.093179 |  | 0.093179 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.039895 |  | 0.039895 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.027765 |  | 0.027765 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.19485 | 0 | 0.19485
FPU-0517 | c | 4DRC | Feeder Recloser | DAPjm | Firmware / Program Update | Feeder Recloser may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.05101 |  | 0.05101 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.13977 |  | 0.13977 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.059842 |  | 0.059842 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.041648 |  | 0.041648 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.29227 | 0 | 0.29227
FPU-0518 | c | 4DCS | Distr. Cust. Storage | DAPjm | Firmware / Program Update | Distr. Cust. Storage may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.7272 |  | 3.7272 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.7272 | 0 | 3.7272
FPU-0519 | c | 4DCG | Distr. Cust. Generation | DAPjm | Firmware / Program Update | Distr. Cust. Generation may be able to process & send NIC firmware update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC firmware update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0511 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0557 | c | 4DRG | DAPjm | Feeder Regulator | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Regulator | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrVR per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0001417 |  | 0.027489 |  | 1.5783e-08 |  | 7.0848 |  | 7.1196 |  | 1.0202 |  | 1.0202 | 461.2359 |  | 0.00038825 |  | 0.07532 |  | 8.4175e-09 |  | 19.4123 |  | 19.5078 |  | 2.7954 |  | 2.7954 | 197.4792 |  | 0.00016623 |  | 0.032248 |  | 5.1536e-10 |  | 8.3114 |  | 8.3523 |  | 1.1968 |  | 1.1968 | 137.437 |  | 0.00011569 |  | 0.022443 |  | 1.1273e-10 |  | 5.7844 |  | 5.8128 |  | 0.83295 |  | 0.83295 | 964.4867 |  | 0.00081186 |  | 0.1575 |  | 7.9113e-10 |  | 40.5929 |  | 40.7926 | 0 | 5.8454 | 0 | 5.8454
FPU-0558 | c | 4DCB | DAPjm | Feeder Cap Bank | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrCB per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.00075571 |  | 0.14661 |  | 8.4175e-08 |  | 37.7855 |  | 37.9715 |  | 5.4411 |  | 5.4411 | 2459.9246 |  | 0.0020706 |  | 0.4017 |  | 4.4893e-08 |  | 103.5322 |  | 104.0416 |  | 14.9086 |  | 14.9086 | 1053.2224 |  | 0.00088655 |  | 0.17199 |  | 2.7486e-09 |  | 44.3275 |  | 44.5456 |  | 6.3832 |  | 6.3832 | 732.9974 |  | 0.000617 |  | 0.1197 |  | 6.0125e-10 |  | 30.8501 |  | 31.0018 |  | 4.4424 |  | 4.4424 | 5143.9289 |  | 0.0043299 |  | 0.84 |  | 4.2194e-09 |  | 216.4953 |  | 217.5605 | 0 | 31.1753 | 0 | 31.1753
FPU-0559 | c | 4DS | DAPjm | Feeder Sensor | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sensor | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrFS per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.00094464 |  | 0.18326 |  | 1.0522e-07 |  | 47.2319 |  | 47.4643 |  | 6.8014 |  | 6.8014 | 3074.9057 |  | 0.0025883 |  | 0.50213 |  | 5.6117e-08 |  | 129.4152 |  | 130.0519 |  | 18.6358 |  | 18.6358 | 1316.5279 |  | 0.0011082 |  | 0.21499 |  | 3.4357e-09 |  | 55.4094 |  | 55.682 |  | 7.979 |  | 7.979 | 916.2467 |  | 0.00077125 |  | 0.14962 |  | 7.5156e-10 |  | 38.5626 |  | 38.7523 |  | 5.553 |  | 5.553 | 6429.9111 |  | 0.0054124 |  | 1.05 |  | 5.2742e-09 |  | 270.6192 |  | 271.9506 | 0 | 38.9692 | 0 | 38.9692
FPU-0560 | c | 4DST | DAPjm | Feeder Sectionalizer | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrST per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrST | fdrST | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0561 | c | 4DSW | DAPjm | Feeder Switch | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Switch | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrSW per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00037786 |  | 0.073304 |  | 4.2088e-08 |  | 18.8928 |  | 18.9857 |  | 2.7206 |  | 2.7206 | 1229.9623 |  | 0.0010353 |  | 0.20085 |  | 2.2447e-08 |  | 51.7661 |  | 52.0208 |  | 7.4543 |  | 7.4543 | 526.6112 |  | 0.00044328 |  | 0.085995 |  | 1.3743e-09 |  | 22.1638 |  | 22.2728 |  | 3.1916 |  | 3.1916 | 366.4987 |  | 0.0003085 |  | 0.059849 |  | 3.0063e-10 |  | 15.425 |  | 15.5009 |  | 2.2212 |  | 2.2212 | 2571.9644 |  | 0.002165 |  | 0.42 |  | 2.1097e-09 |  | 108.2477 |  | 108.7802 | 0 | 15.5877 | 0 | 15.5877
FPU-0562 | c | 4DRC | DAPjm | Feeder Recloser | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Recloser | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrRC per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.00056678 |  | 0.10996 |  | 6.3131e-08 |  | 28.3392 |  | 28.4786 |  | 4.0808 |  | 4.0808 | 1844.9434 |  | 0.001553 |  | 0.30128 |  | 3.367e-08 |  | 77.6491 |  | 78.0312 |  | 11.1815 |  | 11.1815 | 789.9168 |  | 0.00066491 |  | 0.12899 |  | 2.0614e-09 |  | 33.2457 |  | 33.4092 |  | 4.7874 |  | 4.7874 | 549.748 |  | 0.00046275 |  | 0.089774 |  | 4.5094e-10 |  | 23.1375 |  | 23.2514 |  | 3.3318 |  | 3.3318 | 3857.9467 |  | 0.0032474 |  | 0.63 |  | 3.1645e-09 |  | 162.3715 |  | 163.1704 | 0 | 23.3815 | 0 | 23.3815
FPU-0563 | c | 4DCS | DAPjm | Distr. Cust. Storage | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 0.041413 |  | 8.0341 |  | 5.7386e-05 |  | 2070.6436 |  | 2080.8311 |  | 298.1727 |  | 298.1727 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.041413 |  | 8.0341 |  | 4.0356e-08 |  | 2070.6436 |  | 2080.8311 | 0 | 298.1727 | 0 | 298.1727
FPU-0564 | c | 4DCG | DAPjm | Distr. Cust. Generation | Firmware / Program Update | DAPjm may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_program_update_cmd | cmd | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ year | > 99.5% | 10 min - < 2 hr per 1 Distr device | 1k - 50k | year |  |  | X | down |  | x | FPU-0552 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 7200 | 37.1134 | 50000 | 194 |  | 8.4175e-07 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0595 | c | 4DRG | Feeder Regulator | DAPjm | Firmware / Program Update | Feeder Regulator may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.012753 |  | 0.012753 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.034942 |  | 0.034942 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.014961 |  | 0.014961 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.010412 |  | 0.010412 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.073067 | 0 | 0.073067
FPU-0596 | c | 4DCB | Feeder Cap Bank | DAPjm | Firmware / Program Update | Feeder Cap Bank may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.068014 |  | 0.068014 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.18636 |  | 0.18636 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.07979 |  | 0.07979 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.05553 |  | 0.05553 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.38969 | 0 | 0.38969
FPU-0597 | c | 4DS | Feeder Sensor | DAPjm | Firmware / Program Update | Feeder Sensor may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.085017 |  | 0.085017 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.23295 |  | 0.23295 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.099737 |  | 0.099737 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.069413 |  | 0.069413 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.48711 | 0 | 0.48711
FPU-0598 | c | 4DST | Feeder Sectionalizer | DAPjm | Firmware / Program Update | Feeder Sectionalizer may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrST | fdrST | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0599 | c | 4DSW | Feeder Switch | DAPjm | Firmware / Program Update | Feeder Switch may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.034007 |  | 0.034007 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.093179 |  | 0.093179 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.039895 |  | 0.039895 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.027765 |  | 0.027765 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.19485 | 0 | 0.19485
FPU-0600 | c | 4DRC | Feeder Recloser | DAPjm | Firmware / Program Update | Feeder Recloser may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.05101 |  | 0.05101 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.13977 |  | 0.13977 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.059842 |  | 0.059842 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.041648 |  | 0.041648 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.29227 | 0 | 0.29227
FPU-0601 | c | 4DCS | Distr. Cust. Storage | DAPjm | Firmware / Program Update | Distr. Cust. Storage may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.7272 |  | 3.7272 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.7272 | 0 | 3.7272
FPU-0602 | c | 4DCG | Distr. Cust. Generation | DAPjm | Firmware / Program Update | Distr. Cust. Generation may be able to process & send NIC program update confirmation message (per update request from AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC program update | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0594 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0616 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Regulator | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 1.9698 |  | 1.1364e-06 |  | 510.1049 |  | 510.1704 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 5.3972 |  | 6.0606e-07 |  | 1397.6844 |  | 1397.864 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 2.3108 |  | 3.7106e-08 |  | 598.4218 |  | 598.4987 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 1.6082 |  | 8.1169e-09 |  | 416.4758 |  | 416.5293 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 11.286 |  | 5.6962e-08 |  | 2922.6869 |  | 2923.0624 | 0 | 0.4384 | 0 | 0.4384
FPU-0616 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Regulator | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 1.9698 |  | 1.1364e-06 |  | 510.1049 |  | 510.1704 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 5.3972 |  | 6.0606e-07 |  | 1397.6844 |  | 1397.864 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 2.3108 |  | 3.7106e-08 |  | 598.4218 |  | 598.4987 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 1.6082 |  | 8.1169e-09 |  | 416.4758 |  | 416.5293 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 11.286 |  | 5.6962e-08 |  | 2922.6869 |  | 2923.0624 | 0 | 0.4384 | 0 | 0.4384
FPU-0617 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 10.5054 |  | 6.0606e-06 |  | 2720.5594 |  | 2720.909 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 28.7848 |  | 3.2323e-06 |  | 7454.3168 |  | 7455.2747 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 12.3243 |  | 1.979e-07 |  | 3191.5829 |  | 3191.993 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 8.5772 |  | 4.329e-08 |  | 2221.2042 |  | 2221.4896 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 60.1918 |  | 3.0379e-07 |  | 15587.6633 |  | 15589.6663 | 0 | 2.3381 | 0 | 2.3381
FPU-0617 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 10.5054 |  | 6.0606e-06 |  | 2720.5594 |  | 2720.909 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 28.7848 |  | 3.2323e-06 |  | 7454.3168 |  | 7455.2747 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 12.3243 |  | 1.979e-07 |  | 3191.5829 |  | 3191.993 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 8.5772 |  | 4.329e-08 |  | 2221.2042 |  | 2221.4896 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 60.1918 |  | 3.0379e-07 |  | 15587.6633 |  | 15589.6663 | 0 | 2.3381 | 0 | 2.3381
FPU-0618 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sensor | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 13.1318 |  | 7.5758e-06 |  | 3400.6992 |  | 3401.1362 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 35.9811 |  | 4.0404e-06 |  | 9317.896 |  | 9319.0934 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 15.4054 |  | 2.4737e-07 |  | 3989.4786 |  | 3989.9913 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 10.7215 |  | 5.4113e-08 |  | 2776.5052 |  | 2776.862 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 75.2397 |  | 3.7974e-07 |  | 19484.5791 |  | 19487.0828 | 0 | 2.9227 | 0 | 2.9227
FPU-0618 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sensor | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 13.1318 |  | 7.5758e-06 |  | 3400.6992 |  | 3401.1362 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 35.9811 |  | 4.0404e-06 |  | 9317.896 |  | 9319.0934 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 15.4054 |  | 2.4737e-07 |  | 3989.4786 |  | 3989.9913 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 10.7215 |  | 5.4113e-08 |  | 2776.5052 |  | 2776.862 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 75.2397 |  | 3.7974e-07 |  | 19484.5791 |  | 19487.0828 | 0 | 2.9227 | 0 | 2.9227
FPU-0619 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0619 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0620 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Switch | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 5.2527 |  | 3.0303e-06 |  | 1360.2797 |  | 1360.4545 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 14.3924 |  | 1.6162e-06 |  | 3727.1584 |  | 3727.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 6.1621 |  | 9.8949e-08 |  | 1595.7915 |  | 1595.9965 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 4.2886 |  | 2.1645e-08 |  | 1110.6021 |  | 1110.7448 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 30.0959 |  | 1.519e-07 |  | 7793.8316 |  | 7794.8331 | 0 | 1.1691 | 0 | 1.1691
FPU-0620 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Switch | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 5.2527 |  | 3.0303e-06 |  | 1360.2797 |  | 1360.4545 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 14.3924 |  | 1.6162e-06 |  | 3727.1584 |  | 3727.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 6.1621 |  | 9.8949e-08 |  | 1595.7915 |  | 1595.9965 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 4.2886 |  | 2.1645e-08 |  | 1110.6021 |  | 1110.7448 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 30.0959 |  | 1.519e-07 |  | 7793.8316 |  | 7794.8331 | 0 | 1.1691 | 0 | 1.1691
FPU-0621 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Recloser | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 7.8791 |  | 4.5455e-06 |  | 2040.4195 |  | 2040.6817 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 21.5886 |  | 2.4242e-06 |  | 5590.7376 |  | 5591.456 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 9.2432 |  | 1.4842e-07 |  | 2393.6872 |  | 2393.9948 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 6.4329 |  | 3.2468e-08 |  | 1665.9031 |  | 1666.1172 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 45.1438 |  | 2.2785e-07 |  | 11690.7474 |  | 11692.2497 | 0 | 1.7536 | 0 | 1.7536
FPU-0621 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Feeder Recloser | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 7.8791 |  | 4.5455e-06 |  | 2040.4195 |  | 2040.6817 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 21.5886 |  | 2.4242e-06 |  | 5590.7376 |  | 5591.456 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 9.2432 |  | 1.4842e-07 |  | 2393.6872 |  | 2393.9948 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 6.4329 |  | 3.2468e-08 |  | 1665.9031 |  | 1666.1172 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 45.1438 |  | 2.2785e-07 |  | 11690.7474 |  | 11692.2497 | 0 | 1.7536 | 0 | 1.7536
FPU-0622 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 0.0041318 |  | 149086.3365 |  | 149105.4941 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 2.9056e-06 |  | 149086.3365 |  | 149105.4941 | 0 | 22.363 | 0 | 22.363
FPU-0622 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 0.0041318 |  | 149086.3365 |  | 149105.4941 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 2.9056e-06 |  | 149086.3365 |  | 149105.4941 | 0 | 22.363 | 0 | 22.363
FPU-0623 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0623 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0624 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to FAN gateway - sub | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)FANgw per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 8.3982e-08 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 1.879e-10 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 5.9059e-11 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.035105 |  | 1.7718e-10 |  | 9.0909 |  | 9.0921 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0624 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & forward NIC firmware update request (without adversely impacting normal operations) to FAN gateway - sub | NIC_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)FANgw per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0607 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 8.3982e-08 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 1.879e-10 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.011702 |  | 5.9059e-11 |  | 3.0303 |  | 3.0307 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.035105 |  | 1.7718e-10 |  | 9.0909 |  | 9.0921 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0635 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0635 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0636 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0636 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0637 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0637 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0638 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0638 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0639 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0639 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0640 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0640 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0641 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0641 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0642 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0642 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0643 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0643 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send NIC firmware update confirmation message (per update request from Field Tool) to Field Tool | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ NIC firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0626 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0675 | c | 4DRG | Feeder Regulator | DAPjm | Firmware / Program Update | Feeder Regulator may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.012753 |  | 0.012753 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.034942 |  | 0.034942 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.014961 |  | 0.014961 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.010412 |  | 0.010412 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.073067 | 0 | 0.073067
FPU-0676 | c | 4DCB | Feeder Cap Bank | DAPjm | Firmware / Program Update | Feeder Cap Bank may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.068014 |  | 0.068014 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.18636 |  | 0.18636 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.07979 |  | 0.07979 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.05553 |  | 0.05553 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.38969 | 0 | 0.38969
FPU-0677 | c | 4DS | Feeder Sensor | DAPjm | Firmware / Program Update | Feeder Sensor may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.085017 |  | 0.085017 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.23295 |  | 0.23295 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.099737 |  | 0.099737 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.069413 |  | 0.069413 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.48711 | 0 | 0.48711
FPU-0678 | c | 4DST | Feeder Sectionalizer | DAPjm | Firmware / Program Update | Feeder Sectionalizer may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrST | fdrST | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0679 | c | 4DSW | Feeder Switch | DAPjm | Firmware / Program Update | Feeder Switch may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.034007 |  | 0.034007 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.093179 |  | 0.093179 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.039895 |  | 0.039895 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.027765 |  | 0.027765 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.19485 | 0 | 0.19485
FPU-0680 | c | 4DRC | Feeder Recloser | DAPjm | Firmware / Program Update | Feeder Recloser may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.05101 |  | 0.05101 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.13977 |  | 0.13977 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.059842 |  | 0.059842 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.041648 |  | 0.041648 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.29227 | 0 | 0.29227
FPU-0681 | c | 4DCS | Distr. Cust. Storage | DAPjm | Firmware / Program Update | Distr. Cust. Storage may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.7272 |  | 3.7272 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.7272 | 0 | 3.7272
FPU-0682 | c | 4DCG | Distr. Cust. Generation | DAPjm | Firmware / Program Update | Distr. Cust. Generation may be able to process & send NIC firmware update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC firmware update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0674 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0696 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Regulator | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 0.04948 |  | 2.8409e-08 |  | 12.7526 |  | 12.8154 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 0.13558 |  | 1.5152e-08 |  | 34.9421 |  | 35.114 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 0.058047 |  | 9.2764e-10 |  | 14.9605 |  | 15.0342 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 0.040398 |  | 2.0292e-10 |  | 10.4119 |  | 10.4631 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 0.2835 |  | 1.424e-09 |  | 73.0672 |  | 73.4267 | 0 | 0.4384 | 0 | 0.4384
FPU-0696 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Regulator | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 0.04948 |  | 2.8409e-08 |  | 12.7526 |  | 12.8154 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 0.13558 |  | 1.5152e-08 |  | 34.9421 |  | 35.114 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 0.058047 |  | 9.2764e-10 |  | 14.9605 |  | 15.0342 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 0.040398 |  | 2.0292e-10 |  | 10.4119 |  | 10.4631 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 0.2835 |  | 1.424e-09 |  | 73.0672 |  | 73.4267 | 0 | 0.4384 | 0 | 0.4384
FPU-0697 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 0.26389 |  | 1.5152e-07 |  | 68.014 |  | 68.3486 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 0.72307 |  | 8.0808e-08 |  | 186.3579 |  | 187.2748 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 0.30958 |  | 4.9474e-09 |  | 79.7896 |  | 80.1821 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 0.21546 |  | 1.0823e-09 |  | 55.5301 |  | 55.8033 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 1.512 |  | 7.5949e-09 |  | 389.6916 |  | 391.6089 | 0 | 2.3381 | 0 | 2.3381
FPU-0697 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Cap Bank | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 0.26389 |  | 1.5152e-07 |  | 68.014 |  | 68.3486 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 0.72307 |  | 8.0808e-08 |  | 186.3579 |  | 187.2748 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 0.30958 |  | 4.9474e-09 |  | 79.7896 |  | 80.1821 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 0.21546 |  | 1.0823e-09 |  | 55.5301 |  | 55.8033 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 1.512 |  | 7.5949e-09 |  | 389.6916 |  | 391.6089 | 0 | 2.3381 | 0 | 2.3381
FPU-0698 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sensor | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 0.32987 |  | 1.8939e-07 |  | 85.0175 |  | 85.4358 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 0.90384 |  | 1.0101e-07 |  | 232.9474 |  | 234.0935 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 0.38698 |  | 6.1843e-09 |  | 99.737 |  | 100.2277 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 0.26932 |  | 1.3528e-09 |  | 69.4126 |  | 69.7541 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 1.89 |  | 9.4936e-09 |  | 487.1145 |  | 489.5111 | 0 | 2.9227 | 0 | 2.9227
FPU-0698 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sensor | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 0.32987 |  | 1.8939e-07 |  | 85.0175 |  | 85.4358 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 0.90384 |  | 1.0101e-07 |  | 232.9474 |  | 234.0935 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 0.38698 |  | 6.1843e-09 |  | 99.737 |  | 100.2277 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 0.26932 |  | 1.3528e-09 |  | 69.4126 |  | 69.7541 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 1.89 |  | 9.4936e-09 |  | 487.1145 |  | 489.5111 | 0 | 2.9227 | 0 | 2.9227
FPU-0699 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0699 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Sectionalizer | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0700 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Switch | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 0.13195 |  | 7.5758e-08 |  | 34.007 |  | 34.1743 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 0.36153 |  | 4.0404e-08 |  | 93.179 |  | 93.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 0.15479 |  | 2.4737e-09 |  | 39.8948 |  | 40.0911 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 0.10773 |  | 5.4113e-10 |  | 27.7651 |  | 27.9017 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 0.756 |  | 3.7974e-09 |  | 194.8458 |  | 195.8044 | 0 | 1.1691 | 0 | 1.1691
FPU-0700 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Switch | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 0.13195 |  | 7.5758e-08 |  | 34.007 |  | 34.1743 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 0.36153 |  | 4.0404e-08 |  | 93.179 |  | 93.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 0.15479 |  | 2.4737e-09 |  | 39.8948 |  | 40.0911 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 0.10773 |  | 5.4113e-10 |  | 27.7651 |  | 27.9017 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 0.756 |  | 3.7974e-09 |  | 194.8458 |  | 195.8044 | 0 | 1.1691 | 0 | 1.1691
FPU-0701 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Recloser | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 0.19792 |  | 1.1364e-07 |  | 51.0105 |  | 51.2615 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 0.5423 |  | 6.0606e-08 |  | 139.7684 |  | 140.4561 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 0.23219 |  | 3.7106e-09 |  | 59.8422 |  | 60.1366 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 0.16159 |  | 8.1169e-10 |  | 41.6476 |  | 41.8525 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 1.134 |  | 5.6962e-09 |  | 292.2687 |  | 293.7066 | 0 | 1.7536 | 0 | 1.7536
FPU-0701 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Feeder Recloser | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 0.19792 |  | 1.1364e-07 |  | 51.0105 |  | 51.2615 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 0.5423 |  | 6.0606e-08 |  | 139.7684 |  | 140.4561 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 0.23219 |  | 3.7106e-09 |  | 59.8422 |  | 60.1366 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 0.16159 |  | 8.1169e-10 |  | 41.6476 |  | 41.8525 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 1.134 |  | 5.6962e-09 |  | 292.2687 |  | 293.7066 | 0 | 1.7536 | 0 | 1.7536
FPU-0702 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 0.0001033 |  | 3727.1584 |  | 3745.496 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 7.264e-08 |  | 3727.1584 |  | 3745.496 | 0 | 22.363 | 0 | 22.363
FPU-0702 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Storage | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 0.0001033 |  | 3727.1584 |  | 3745.496 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 7.264e-08 |  | 3727.1584 |  | 3745.496 | 0 | 22.363 | 0 | 22.363
FPU-0703 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0703 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to Distr. Cust. Generation | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0704 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to FAN gateway - sub | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)FANgw per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | up |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 2.0996e-09 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 4.6974e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 1.4765e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.00088182 |  | 4.4294e-12 |  | 0.22727 |  | 0.22839 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0704 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & forward NIC program update request (without adversely impacting normal operations) to FAN gateway - sub | NIC_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)FANgw per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 1k - 50k | year |  |  | X | down |  | x | FPU-0687 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 2.0996e-09 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 4.6974e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 1.4765e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.00088182 |  | 4.4294e-12 |  | 0.22727 |  | 0.22839 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0715 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0715 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0716 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0716 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0717 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0717 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0718 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0718 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0719 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0719 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0720 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0720 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0721 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0721 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0722 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0722 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0723 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0723 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send NIC program update confirmation message (per update request from Field Tool) to Field Tool | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ NIC program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0706 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0755 | c | 4DRG | Feeder Regulator | DAPjm | Firmware / Program Update | Feeder Regulator may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrVR | fdrVR | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.012753 |  | 0.012753 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.034942 |  | 0.034942 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.014961 |  | 0.014961 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.010412 |  | 0.010412 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.073067 | 0 | 0.073067
FPU-0756 | c | 4DCB | Feeder Cap Bank | DAPjm | Firmware / Program Update | Feeder Cap Bank may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrCB | fdrCB | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.068014 |  | 0.068014 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.18636 |  | 0.18636 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.07979 |  | 0.07979 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.05553 |  | 0.05553 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.38969 | 0 | 0.38969
FPU-0757 | c | 4DS | Feeder Sensor | DAPjm | Firmware / Program Update | Feeder Sensor may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrFS | fdrFS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.085017 |  | 0.085017 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.23295 |  | 0.23295 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.099737 |  | 0.099737 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.069413 |  | 0.069413 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.48711 | 0 | 0.48711
FPU-0758 | c | 4DST | Feeder Sectionalizer | DAPjm | Firmware / Program Update | Feeder Sectionalizer may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrST | fdrST | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0759 | c | 4DSW | Feeder Switch | DAPjm | Firmware / Program Update | Feeder Switch may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrSW | fdrSW | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.034007 |  | 0.034007 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.093179 |  | 0.093179 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.039895 |  | 0.039895 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.027765 |  | 0.027765 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.19485 | 0 | 0.19485
FPU-0760 | c | 4DRC | Feeder Recloser | DAPjm | Firmware / Program Update | Feeder Recloser may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrRC | fdrRC | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.05101 |  | 0.05101 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.13977 |  | 0.13977 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.059842 |  | 0.059842 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.041648 |  | 0.041648 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.29227 | 0 | 0.29227
FPU-0761 | c | 4DCS | Distr. Cust. Storage | DAPjm | Firmware / Program Update | Distr. Cust. Storage may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrDCS | fdrDCS | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.7272 |  | 3.7272 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.7272 | 0 | 3.7272
FPU-0762 | c | 4DCG | Distr. Cust. Generation | DAPjm | Firmware / Program Update | Distr. Cust. Generation may be able to process & send NIC program update confirmation message (per update request from Field Tool as alternate to AMI Head-End(j)) to DAPjm | NIC_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ NIC program update from Field Tool | > 99.5% | < 3 sec | 50 | request |  |  | X | up |  | x | FPU-0754 |  |  | 0.090909 | 1 | fdrDCG | fdrDCG | 3 | 3 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0772 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & send FAN Gateway firmware update request (without adversely impacting normal operations) to FAN gateway - sub | FAN-GtWay_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)RTU-Sub(x)FANgw per ¦ firmware or program update from Field Tool cycle per year | > 99.5% | < 10 min | 400k - 750k | year |  |  | X | up |  | x | FPU-0771 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool | 300 | 0.10359 | 750000 | 2896 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 3.1493e-08 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 7.0461e-11 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 2.2147e-11 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.013164 |  | 6.6441e-11 |  | 3.4091 |  | 3.4094 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0772 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & send FAN Gateway firmware update request (without adversely impacting normal operations) to FAN gateway - sub | FAN-GtWay_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)RTU-Sub(x)FANgw per ¦ firmware or program update from Field Tool cycle per year | > 99.5% | < 10 min | 400k - 750k | year |  |  | X | down |  | x | FPU-0771 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool | 300 | 0.10359 | 750000 | 2896 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 3.1493e-08 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 7.0461e-11 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.0043879 |  | 2.2147e-11 |  | 1.1364 |  | 1.1365 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.013164 |  | 6.6441e-11 |  | 3.4091 |  | 3.4094 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0775 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send FAN Gateway firmware update confirmation message (per update request from Field Tool) to Field Tool | FAN-GtWay_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0774 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0775 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send FAN Gateway firmware update confirmation message (per update request from Field Tool) to Field Tool | FAN-GtWay_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0774 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0787 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & send FAN Gateway program update request (without adversely impacting normal operations) to FAN gateway - sub | FAN-GtWay_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)RTU-Sub(x)FANgw per ¦ firmware or program update from Field Tool cycle per year | > 99.5% | < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0786 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 2.0996e-09 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 4.6974e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 1.4765e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.00088182 |  | 4.4294e-12 |  | 0.22727 |  | 0.22839 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0787 | c | 6FFGa | Field Tool | FAN gateway - sub | Firmware / Program Update | Field Tool may be able to process & send FAN Gateway program update request (without adversely impacting normal operations) to FAN gateway - sub | FAN-GtWay_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ Sub(x)RTU-Sub(x)FANgw per ¦ firmware or program update from Field Tool cycle per year | > 99.5% | < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0786 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)RTU-Sub(x)FANgw-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 2.0996e-09 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 4.6974e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 1 |  | 1.5152e-06 |  | 0.00029394 |  | 1.4765e-12 |  | 0.075758 |  | 0.07613 |  | 0.00045455 |  | 0.00045455 | 3 |  | 4.5455e-06 |  | 0.00088182 |  | 4.4294e-12 |  | 0.22727 |  | 0.22839 | 0 | 0.0013636 | 0 | 0.0013636
FPU-0790 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send FAN Gateway program update confirmation message (per update request from Field Tool) to Field Tool | FAN-GtWay_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0789 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0790 | c | 6FFGa | FAN gateway - sub | Field Tool | Firmware / Program Update | FAN gateway - sub shall be able to process & send FAN Gateway program update confirmation message (per update request from Field Tool) to Field Tool | FAN-GtWay_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ Sub(x)FANgw per ¦ program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0789 | D | 0.5 | 0.090909 | 1 | Sub(x)FANgw | Sub(x)FANgw-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 3.4993e-11 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 7.829e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 1 |  | 2.5253e-05 |  | 2.5253e-05 |  | 2.4608e-14 |  | 0.0012626 |  | 0.0012626 |  | 6.3131e-05 |  | 6.3131e-05 | 3 |  | 7.5758e-05 |  | 7.5758e-05 |  | 7.3824e-14 |  | 0.0037879 |  | 0.0037879 | 0 | 0.00018939 | 0 | 0.00018939
FPU-0920 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Regulator | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 1.9698 |  | 1.1364e-06 |  | 510.1049 |  | 510.1704 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 5.3972 |  | 6.0606e-07 |  | 1397.6844 |  | 1397.864 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 2.3108 |  | 3.7106e-08 |  | 598.4218 |  | 598.4987 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 1.6082 |  | 8.1169e-09 |  | 416.4758 |  | 416.5293 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 11.286 |  | 5.6962e-08 |  | 2922.6869 |  | 2923.0624 | 0 | 0.4384 | 0 | 0.4384
FPU-0920 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Regulator | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 1.9698 |  | 1.1364e-06 |  | 510.1049 |  | 510.1704 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 5.3972 |  | 6.0606e-07 |  | 1397.6844 |  | 1397.864 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 2.3108 |  | 3.7106e-08 |  | 598.4218 |  | 598.4987 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 1.6082 |  | 8.1169e-09 |  | 416.4758 |  | 416.5293 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 11.286 |  | 5.6962e-08 |  | 2922.6869 |  | 2923.0624 | 0 | 0.4384 | 0 | 0.4384
FPU-0921 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Cap Bank | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 10.5054 |  | 6.0606e-06 |  | 2720.5594 |  | 2720.909 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 28.7848 |  | 3.2323e-06 |  | 7454.3168 |  | 7455.2747 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 12.3243 |  | 1.979e-07 |  | 3191.5829 |  | 3191.993 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 8.5772 |  | 4.329e-08 |  | 2221.2042 |  | 2221.4896 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 60.1918 |  | 3.0379e-07 |  | 15587.6633 |  | 15589.6663 | 0 | 2.3381 | 0 | 2.3381
FPU-0921 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Cap Bank | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 10.5054 |  | 6.0606e-06 |  | 2720.5594 |  | 2720.909 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 28.7848 |  | 3.2323e-06 |  | 7454.3168 |  | 7455.2747 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 12.3243 |  | 1.979e-07 |  | 3191.5829 |  | 3191.993 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 8.5772 |  | 4.329e-08 |  | 2221.2042 |  | 2221.4896 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 60.1918 |  | 3.0379e-07 |  | 15587.6633 |  | 15589.6663 | 0 | 2.3381 | 0 | 2.3381
FPU-0922 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Sensor | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 13.1318 |  | 7.5758e-06 |  | 3400.6992 |  | 3401.1362 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 35.9811 |  | 4.0404e-06 |  | 9317.896 |  | 9319.0934 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 15.4054 |  | 2.4737e-07 |  | 3989.4786 |  | 3989.9913 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 10.7215 |  | 5.4113e-08 |  | 2776.5052 |  | 2776.862 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 75.2397 |  | 3.7974e-07 |  | 19484.5791 |  | 19487.0828 | 0 | 2.9227 | 0 | 2.9227
FPU-0922 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Sensor | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 13.1318 |  | 7.5758e-06 |  | 3400.6992 |  | 3401.1362 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 35.9811 |  | 4.0404e-06 |  | 9317.896 |  | 9319.0934 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 15.4054 |  | 2.4737e-07 |  | 3989.4786 |  | 3989.9913 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 10.7215 |  | 5.4113e-08 |  | 2776.5052 |  | 2776.862 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 75.2397 |  | 3.7974e-07 |  | 19484.5791 |  | 19487.0828 | 0 | 2.9227 | 0 | 2.9227
FPU-0923 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Sectionalizer | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0923 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Sectionalizer | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0924 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Switch | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 5.2527 |  | 3.0303e-06 |  | 1360.2797 |  | 1360.4545 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 14.3924 |  | 1.6162e-06 |  | 3727.1584 |  | 3727.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 6.1621 |  | 9.8949e-08 |  | 1595.7915 |  | 1595.9965 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 4.2886 |  | 2.1645e-08 |  | 1110.6021 |  | 1110.7448 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 30.0959 |  | 1.519e-07 |  | 7793.8316 |  | 7794.8331 | 0 | 1.1691 | 0 | 1.1691
FPU-0924 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Switch | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 5.2527 |  | 3.0303e-06 |  | 1360.2797 |  | 1360.4545 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 14.3924 |  | 1.6162e-06 |  | 3727.1584 |  | 3727.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 6.1621 |  | 9.8949e-08 |  | 1595.7915 |  | 1595.9965 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 4.2886 |  | 2.1645e-08 |  | 1110.6021 |  | 1110.7448 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 30.0959 |  | 1.519e-07 |  | 7793.8316 |  | 7794.8331 | 0 | 1.1691 | 0 | 1.1691
FPU-0925 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Recloser | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 7.8791 |  | 4.5455e-06 |  | 2040.4195 |  | 2040.6817 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 21.5886 |  | 2.4242e-06 |  | 5590.7376 |  | 5591.456 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 9.2432 |  | 1.4842e-07 |  | 2393.6872 |  | 2393.9948 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 6.4329 |  | 3.2468e-08 |  | 1665.9031 |  | 1666.1172 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 45.1438 |  | 2.2785e-07 |  | 11690.7474 |  | 11692.2497 | 0 | 1.7536 | 0 | 1.7536
FPU-0925 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Feeder Recloser | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 7.8791 |  | 4.5455e-06 |  | 2040.4195 |  | 2040.6817 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 21.5886 |  | 2.4242e-06 |  | 5590.7376 |  | 5591.456 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 9.2432 |  | 1.4842e-07 |  | 2393.6872 |  | 2393.9948 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 6.4329 |  | 3.2468e-08 |  | 1665.9031 |  | 1666.1172 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 45.1438 |  | 2.2785e-07 |  | 11690.7474 |  | 11692.2497 | 0 | 1.7536 | 0 | 1.7536
FPU-0926 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Distr. Cust. Storage | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 0.0041318 |  | 149086.3365 |  | 149105.4941 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 2.9056e-06 |  | 149086.3365 |  | 149105.4941 | 0 | 22.363 | 0 | 22.363
FPU-0926 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Distr. Cust. Storage | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ NIC firmware or program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 0.0041318 |  | 149086.3365 |  | 149105.4941 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 575.6969 |  | 2.9056e-06 |  | 149086.3365 |  | 149105.4941 | 0 | 22.363 | 0 | 22.363
FPU-0927 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Distr. Cust. Generation | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | up |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0927 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller firmware update request (without adversely impacting normal operations) to Distr. Cust. Generation | Fdr-dev-cntl_firmware_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ NIC firmware or programupdate cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 400k - 2,000k | year |  |  | X | down |  | x | FPU-0911 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 0.038845 | 2000000 | 7723 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0939 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0939 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-0940 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0940 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-0941 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0941 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-0942 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0942 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0943 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0943 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-0944 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0944 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-0945 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0945 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-0946 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0946 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send Feeder device controller firmware update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_firmware_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ cntl firmware update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0930 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0987 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Regulator | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 0.04948 |  | 2.8409e-08 |  | 12.7526 |  | 12.8154 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 0.13558 |  | 1.5152e-08 |  | 34.9421 |  | 35.114 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 0.058047 |  | 9.2764e-10 |  | 14.9605 |  | 15.0342 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 0.040398 |  | 2.0292e-10 |  | 10.4119 |  | 10.4631 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 0.2835 |  | 1.424e-09 |  | 73.0672 |  | 73.4267 | 0 | 0.4384 | 0 | 0.4384
FPU-0987 | c | 6FRG | Field Tool | Feeder Regulator | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Regulator | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrVR per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.00025505 |  | 0.04948 |  | 2.8409e-08 |  | 12.7526 |  | 12.8154 |  | 0.076516 |  | 0.076516 | 461.2359 |  | 0.00069884 |  | 0.13558 |  | 1.5152e-08 |  | 34.9421 |  | 35.114 |  | 0.20965 |  | 0.20965 | 197.4792 |  | 0.00029921 |  | 0.058047 |  | 9.2764e-10 |  | 14.9605 |  | 15.0342 |  | 0.089763 |  | 0.089763 | 137.437 |  | 0.00020824 |  | 0.040398 |  | 2.0292e-10 |  | 10.4119 |  | 10.4631 |  | 0.062471 |  | 0.062471 | 964.4867 |  | 0.0014613 |  | 0.2835 |  | 1.424e-09 |  | 73.0672 |  | 73.4267 | 0 | 0.4384 | 0 | 0.4384
FPU-0988 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Cap Bank | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 0.26389 |  | 1.5152e-07 |  | 68.014 |  | 68.3486 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 0.72307 |  | 8.0808e-08 |  | 186.3579 |  | 187.2748 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 0.30958 |  | 4.9474e-09 |  | 79.7896 |  | 80.1821 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 0.21546 |  | 1.0823e-09 |  | 55.5301 |  | 55.8033 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 1.512 |  | 7.5949e-09 |  | 389.6916 |  | 391.6089 | 0 | 2.3381 | 0 | 2.3381
FPU-0988 | c | 6FCB | Field Tool | Feeder Cap Bank | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Cap Bank | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrCB per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.0013603 |  | 0.26389 |  | 1.5152e-07 |  | 68.014 |  | 68.3486 |  | 0.40808 |  | 0.40808 | 2459.9246 |  | 0.0037272 |  | 0.72307 |  | 8.0808e-08 |  | 186.3579 |  | 187.2748 |  | 1.1181 |  | 1.1181 | 1053.2224 |  | 0.0015958 |  | 0.30958 |  | 4.9474e-09 |  | 79.7896 |  | 80.1821 |  | 0.47874 |  | 0.47874 | 732.9974 |  | 0.0011106 |  | 0.21546 |  | 1.0823e-09 |  | 55.5301 |  | 55.8033 |  | 0.33318 |  | 0.33318 | 5143.9289 |  | 0.0077938 |  | 1.512 |  | 7.5949e-09 |  | 389.6916 |  | 391.6089 | 0 | 2.3381 | 0 | 2.3381
FPU-0989 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Sensor | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 0.32987 |  | 1.8939e-07 |  | 85.0175 |  | 85.4358 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 0.90384 |  | 1.0101e-07 |  | 232.9474 |  | 234.0935 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 0.38698 |  | 6.1843e-09 |  | 99.737 |  | 100.2277 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 0.26932 |  | 1.3528e-09 |  | 69.4126 |  | 69.7541 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 1.89 |  | 9.4936e-09 |  | 487.1145 |  | 489.5111 | 0 | 2.9227 | 0 | 2.9227
FPU-0989 | c | 6FS | Field Tool | Feeder Sensor | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Sensor | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrFS per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.0017003 |  | 0.32987 |  | 1.8939e-07 |  | 85.0175 |  | 85.4358 |  | 0.5101 |  | 0.5101 | 3074.9057 |  | 0.0046589 |  | 0.90384 |  | 1.0101e-07 |  | 232.9474 |  | 234.0935 |  | 1.3977 |  | 1.3977 | 1316.5279 |  | 0.0019947 |  | 0.38698 |  | 6.1843e-09 |  | 99.737 |  | 100.2277 |  | 0.59842 |  | 0.59842 | 916.2467 |  | 0.0013883 |  | 0.26932 |  | 1.3528e-09 |  | 69.4126 |  | 69.7541 |  | 0.41648 |  | 0.41648 | 6429.9111 |  | 0.0097423 |  | 1.89 |  | 9.4936e-09 |  | 487.1145 |  | 489.5111 | 0 | 2.9227 | 0 | 2.9227
FPU-0990 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Sectionalizer | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0990 | c | 6FST | Field Tool | Feeder Sectionalizer | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Sectionalizer | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrST per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0991 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Switch | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 0.13195 |  | 7.5758e-08 |  | 34.007 |  | 34.1743 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 0.36153 |  | 4.0404e-08 |  | 93.179 |  | 93.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 0.15479 |  | 2.4737e-09 |  | 39.8948 |  | 40.0911 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 0.10773 |  | 5.4113e-10 |  | 27.7651 |  | 27.9017 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 0.756 |  | 3.7974e-09 |  | 194.8458 |  | 195.8044 | 0 | 1.1691 | 0 | 1.1691
FPU-0991 | c | 6FSW | Field Tool | Feeder Switch | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Switch | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrSW per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.00068014 |  | 0.13195 |  | 7.5758e-08 |  | 34.007 |  | 34.1743 |  | 0.20404 |  | 0.20404 | 1229.9623 |  | 0.0018636 |  | 0.36153 |  | 4.0404e-08 |  | 93.179 |  | 93.6374 |  | 0.55907 |  | 0.55907 | 526.6112 |  | 0.0007979 |  | 0.15479 |  | 2.4737e-09 |  | 39.8948 |  | 40.0911 |  | 0.23937 |  | 0.23937 | 366.4987 |  | 0.0005553 |  | 0.10773 |  | 5.4113e-10 |  | 27.7651 |  | 27.9017 |  | 0.16659 |  | 0.16659 | 2571.9644 |  | 0.0038969 |  | 0.756 |  | 3.7974e-09 |  | 194.8458 |  | 195.8044 | 0 | 1.1691 | 0 | 1.1691
FPU-0992 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Recloser | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 0.19792 |  | 1.1364e-07 |  | 51.0105 |  | 51.2615 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 0.5423 |  | 6.0606e-08 |  | 139.7684 |  | 140.4561 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 0.23219 |  | 3.7106e-09 |  | 59.8422 |  | 60.1366 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 0.16159 |  | 8.1169e-10 |  | 41.6476 |  | 41.8525 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 1.134 |  | 5.6962e-09 |  | 292.2687 |  | 293.7066 | 0 | 1.7536 | 0 | 1.7536
FPU-0992 | c | 6FRC | Field Tool | Feeder Recloser | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Feeder Recloser | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrRC per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.0010202 |  | 0.19792 |  | 1.1364e-07 |  | 51.0105 |  | 51.2615 |  | 0.30606 |  | 0.30606 | 1844.9434 |  | 0.0027954 |  | 0.5423 |  | 6.0606e-08 |  | 139.7684 |  | 140.4561 |  | 0.83861 |  | 0.83861 | 789.9168 |  | 0.0011968 |  | 0.23219 |  | 3.7106e-09 |  | 59.8422 |  | 60.1366 |  | 0.35905 |  | 0.35905 | 549.748 |  | 0.00083295 |  | 0.16159 |  | 8.1169e-10 |  | 41.6476 |  | 41.8525 |  | 0.24989 |  | 0.24989 | 3857.9467 |  | 0.0058454 |  | 1.134 |  | 5.6962e-09 |  | 292.2687 |  | 293.7066 | 0 | 1.7536 | 0 | 1.7536
FPU-0993 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Distr. Cust. Storage | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 0.0001033 |  | 3727.1584 |  | 3745.496 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 7.264e-08 |  | 3727.1584 |  | 3745.496 | 0 | 22.363 | 0 | 22.363
FPU-0993 | c | 6FCS | Field Tool | Distr. Cust. Storage | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Distr. Cust. Storage | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCS per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 0.0001033 |  | 3727.1584 |  | 3745.496 |  | 22.363 |  | 22.363 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 0.074543 |  | 14.4614 |  | 7.264e-08 |  | 3727.1584 |  | 3745.496 | 0 | 22.363 | 0 | 22.363
FPU-0994 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Distr. Cust. Generation | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | up |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-0994 | c | 6FCG | Field Tool | Distr. Cust. Generation | Firmware / Program Update | Field Tool may be able to process & forward Feeder device controller program update request (without adversely impacting normal operations) to Distr. Cust. Generation | Fdr-dev-cntl_program_update_cmd | cmd | 7AM - 6PM | 60 per 1000 per ¦ fdrDCG per ¦ cntl program update cycle from Field Tool per year | > 99.5% | 2 min - < 10 min | 25k - 50k | year |  |  | X | down |  | x | FPU-0978 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 300 | 1.5464 | 50000 | 194 |  | 1.5152e-06 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-1006 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-1006 | c | 6FRG | Feeder Regulator | Field Tool | Firmware / Program Update | Feeder Regulator shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrVR per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrVR | fdrVR-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 168.3346 |  | 0.0042509 |  | 0.0042509 |  | 4.7348e-10 |  | 0.21254 |  | 0.21254 |  | 0.010627 |  | 0.010627 | 461.2359 |  | 0.011647 |  | 0.011647 |  | 2.5253e-10 |  | 0.58237 |  | 0.58237 |  | 0.029118 |  | 0.029118 | 197.4792 |  | 0.0049868 |  | 0.0049868 |  | 1.5461e-11 |  | 0.24934 |  | 0.24934 |  | 0.012467 |  | 0.012467 | 137.437 |  | 0.0034706 |  | 0.0034706 |  | 3.382e-12 |  | 0.17353 |  | 0.17353 |  | 0.0086766 |  | 0.0086766 | 964.4867 |  | 0.024356 |  | 0.024356 |  | 2.3734e-11 |  | 1.2178 |  | 1.2178 | 0 | 0.060889 | 0 | 0.060889
FPU-1007 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-1007 | c | 6FCB | Feeder Cap Bank | Field Tool | Firmware / Program Update | Feeder Cap Bank shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrCB per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrCB | fdrCB-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 897.7846 |  | 0.022671 |  | 0.022671 |  | 2.5253e-09 |  | 1.1336 |  | 1.1336 |  | 0.056678 |  | 0.056678 | 2459.9246 |  | 0.062119 |  | 0.062119 |  | 1.3468e-09 |  | 3.106 |  | 3.106 |  | 0.1553 |  | 0.1553 | 1053.2224 |  | 0.026597 |  | 0.026597 |  | 8.2457e-11 |  | 1.3298 |  | 1.3298 |  | 0.066491 |  | 0.066491 | 732.9974 |  | 0.01851 |  | 0.01851 |  | 1.8038e-11 |  | 0.9255 |  | 0.9255 |  | 0.046275 |  | 0.046275 | 5143.9289 |  | 0.1299 |  | 0.1299 |  | 1.2658e-10 |  | 6.4949 |  | 6.4949 | 0 | 0.32474 | 0 | 0.32474
FPU-1008 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-1008 | c | 6FS | Feeder Sensor | Field Tool | Firmware / Program Update | Feeder Sensorshall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrFS per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrFS | fdrFS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 1122.2307 |  | 0.028339 |  | 0.028339 |  | 3.1566e-09 |  | 1.417 |  | 1.417 |  | 0.070848 |  | 0.070848 | 3074.9057 |  | 0.077649 |  | 0.077649 |  | 1.6835e-09 |  | 3.8825 |  | 3.8825 |  | 0.19412 |  | 0.19412 | 1316.5279 |  | 0.033246 |  | 0.033246 |  | 1.0307e-10 |  | 1.6623 |  | 1.6623 |  | 0.083114 |  | 0.083114 | 916.2467 |  | 0.023138 |  | 0.023138 |  | 2.2547e-11 |  | 1.1569 |  | 1.1569 |  | 0.057844 |  | 0.057844 | 6429.9111 |  | 0.16237 |  | 0.16237 |  | 1.5823e-10 |  | 8.1186 |  | 8.1186 | 0 | 0.40593 | 0 | 0.40593
FPU-1009 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-1009 | c | 6FST | Feeder Sectionalizer | Field Tool | Firmware / Program Update | Feeder Sectionalizer shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrST per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrST | fdrST-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-1010 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-1010 | c | 6FSW | Feeder Switch | Field Tool | Firmware / Program Update | Feeder Switch shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrSW per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrSW | fdrSW-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 448.8923 |  | 0.011336 |  | 0.011336 |  | 1.2626e-09 |  | 0.56678 |  | 0.56678 |  | 0.028339 |  | 0.028339 | 1229.9623 |  | 0.03106 |  | 0.03106 |  | 6.734e-10 |  | 1.553 |  | 1.553 |  | 0.077649 |  | 0.077649 | 526.6112 |  | 0.013298 |  | 0.013298 |  | 4.1229e-11 |  | 0.66491 |  | 0.66491 |  | 0.033246 |  | 0.033246 | 366.4987 |  | 0.009255 |  | 0.009255 |  | 9.0188e-12 |  | 0.46275 |  | 0.46275 |  | 0.023138 |  | 0.023138 | 2571.9644 |  | 0.064949 |  | 0.064949 |  | 6.3291e-11 |  | 3.2474 |  | 3.2474 | 0 | 0.16237 | 0 | 0.16237
FPU-1011 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-1011 | c | 6FRC | Feeder Recloser | Field Tool | Firmware / Program Update | Feeder Recloser shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrRC per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrRC | fdrRC-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 | 673.3384 |  | 0.017003 |  | 0.017003 |  | 1.8939e-09 |  | 0.85017 |  | 0.85017 |  | 0.042509 |  | 0.042509 | 1844.9434 |  | 0.046589 |  | 0.046589 |  | 1.0101e-09 |  | 2.3295 |  | 2.3295 |  | 0.11647 |  | 0.11647 | 789.9168 |  | 0.019947 |  | 0.019947 |  | 6.1843e-11 |  | 0.99737 |  | 0.99737 |  | 0.049868 |  | 0.049868 | 549.748 |  | 0.013883 |  | 0.013883 |  | 1.3528e-11 |  | 0.69413 |  | 0.69413 |  | 0.034706 |  | 0.034706 | 3857.9467 |  | 0.097423 |  | 0.097423 |  | 9.4936e-11 |  | 4.8711 |  | 4.8711 | 0 | 0.24356 | 0 | 0.24356
FPU-1012 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-1012 | c | 6FCS | Distr. Cust. Storage | Field Tool | Firmware / Program Update | Distr. Cust. Storage shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCS per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrDCS | fdrDCS-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.7216e-06 |  | 62.1193 |  | 62.1193 |  | 3.106 |  | 3.106 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 49198.4911 |  | 1.2424 |  | 1.2424 |  | 1.2107e-09 |  | 62.1193 |  | 62.1193 | 0 | 3.106 | 0 | 3.106
FPU-1013 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | up |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
FPU-1013 | c | 6FCG | Distr. Cust. Generation | Field Tool | Firmware / Program Update | Distr. Cust. Generation shall be able to process & send Feeder device controller program update confirmation message (per update request from Field Tool) to Field Tool | Fdr-dev-cntl_program_update_confirmation | resp-data | 7AM - 6PM | 1 per ¦ fdrDCG per ¦ cntl program update from Field Tool | > 99.5% | < 5 sec | 50 | request |  |  | X | down |  | x | FPU-0997 | D | 0.5 | 0.090909 | 1 | fdrDCG | fdrDCG-update-from-FieldTool | 2.5 | 2.5 | 50 | 1 |  | 2.5253e-05 | [12 empty] | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [11 empty] | 0 | 0 | 0 | 0
IDCS-019 | c | 4DCS | Distr. Cust. Storage | DAPjm | Islanded Distr. Cust. Storage | Distr. Cust. Storage may be able to process & send Distr. Cust. Storage unit in island mode alarm to DAPjm | distr_cust_storage_in-island-mode_alarm | alarm | 24x7 | 1 per ¦ DAPjm-fdrDCS per ¦ detected-transformer-lose-of-power-event | > 98% | < 4 sec | 50 | event |  | X | X | up |  | x | IDCS-017 |  |  | 0.041667 | 1 | fdrDCS | fdrDCS_detected-transformer-lose-of-power-event | 4 | 4 | 50 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 1.5781e-10 | 3.9453e-07 | 0.0056943 | 14.2357 | 0.0056943 | 14.2357 | 0.00045554 | 1.1389 | 0.00045554 | 1.1389 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 1.1098e-13 | 2.7745e-10 | 0.0056943 | 14.2357 | 0.0056943 | 14.2357 | 0.00045554 | 1.1389 | 0.00045554 | 1.1389
IDCS-031 | c | 1D | DAPjm | 2-Way Meter - Electr | Islanded Distr. Cust. Storage | DAPjm shall be able to process & forward Meter into capped xkwh mode request to 2-Way Meter - Electr | meter_capped_kwh_mode_cmd | cmd | 24x7 | 4-6 per ¦ fdrDCS per ¦ detected-transformer-lose-of-power-event | > 98% | < 5 sec | 25 | event |  | X | X | down |  | x | IDCS-025 |  |  | 0.041667 | 1 | fdrDCS | fdrDCS-detected-lose-of-power | 5 | 5 | 25 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 7.8906e-11 | 1.9726e-07 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 5.5489e-14 | 1.3872e-10 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236
IDCS-033 | c | 1D | 2-Way Meter - Electr | DAPjm | Islanded Distr. Cust. Storage | 2-Way Meter - Electr shall be able to process & send Meter into capped xkwh mode request acknowledgment to DAPjm | meter_capped_kwh_mode_cmd_ack | ack | 24x7 | 1 per ¦ ElectrMtr per ¦ processed capped kwh mode cmd | > 98% | < 5 sec | 25 | cmd |  | X | X | up |  | x | IDCS-032 |  |  | 0.041667 | 1 | ElectrMtr | fdrDCS-ElectrMtr | 5 | 5 | 25 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 3.9453e-10 | 9.8632e-07 | 0.014236 | 35.5892 | 0.014236 | 35.5892 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 2.7745e-13 | 6.9361e-10 | 0.014236 | 35.5892 | 0.014236 | 35.5892 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178
IDCS-043 | c | 1D | 2-Way Meter - Electr | DAPjm | Islanded Distr. Cust. Storage | 2-Way Meter - Electr shall be able to process & send Meter in capped kwh mode alert to DAPjm | meter_in_capped_kwh_mode_alert | alert | 24x7 | 1 per ¦ ElectrMtr-with-IPD-or-CustEMS per ¦ capped kwh mode cmd | > 99% | < 5 sec | 50 - 150 | cmd |  | X | X | up |  | x | IDCS-040 |  |  | 0.041667 | 1 | ElectrMtr | fdrDCS-ElectrMtr-with-IPD-or-CustEMS | 5 | 5 | 150 | 1 | 8.8359e-10 | 1.29e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 1.2322e-08 | 1.7991e-05 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 8.6654e-12 | 1.2652e-08 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382
IDCS-074 | c | 4DCS | Distr. Cust. Storage | DAPjm | Islanded Distr. Cust. Storage | Distr. Cust. Storage may be able to process & send Distr. Cust. Storage unit out of island mode alarm to DAPjm | distr_cust_storage_out-of-island-mode_alert | alert | 24x7 | 1 per ¦ fdrDCS per ¦ detected transformer restore of power event | > 98% | < 4 sec | 50 | event |  | X | X | up |  | x | IDCS-072 |  |  | 0.041667 | 1 | fdrDCS | fdrDCS-detected-lose-of-power | 4 | 4 | 50 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 1.5781e-10 | 3.9453e-07 | 0.0056943 | 14.2357 | 0.0056943 | 14.2357 | 0.00045554 | 1.1389 | 0.00045554 | 1.1389 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 1.1098e-13 | 2.7745e-10 | 0.0056943 | 14.2357 | 0.0056943 | 14.2357 | 0.00045554 | 1.1389 | 0.00045554 | 1.1389
IDCS-086 | c | 1D | DAPjm | 2-Way Meter - Electr | Islanded Distr. Cust. Storage | DAPjm shall be able to process & forward Meter into capped xkwh mode cancel request to 2-Way Meter - Electr | meter_capped_kwh_mode_cancel_cmd | cmd | 24x7 | 4-6 per ¦ fdrDCS per ¦ detected transformer restore of power event | > 98% | < 5 sec | 25 | event |  | X | X | down |  | x | IDCS-080 |  |  | 0.041667 | 1 | fdrDCS | fdrDCS-detected-lose-of-power | 5 | 5 | 25 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 7.8906e-11 | 1.9726e-07 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49198.4911 | 0.00011389 | 0.28471 | 0.00011389 | 0.28471 | 5.5489e-14 | 1.3872e-10 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236
IDCS-088 | c | 1D | 2-Way Meter - Electr | DAPjm | Islanded Distr. Cust. Storage | 2-Way Meter - Electr shall be able to process & send Meter into capped xkwh mode cancel request acknowledgment to DAPjm | meter_capped_kwh_mode_cancel_cmd_ack | ack | 24x7 | 1 per ¦ ElectrMtr per ¦ capped kwh mode cancel cmd | > 98% | < 5 sec | 25 | cmd |  | X | X | up |  | x | IDCS-087 |  |  | 0.041667 | 1 | ElectrMtr | fdrDCS-ElectrMtr | 5 | 5 | 25 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 3.9453e-10 | 9.8632e-07 | 0.014236 | 35.5892 | 0.014236 | 35.5892 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 2.7745e-13 | 6.9361e-10 | 0.014236 | 35.5892 | 0.014236 | 35.5892 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178
IDCS-098 | c | 1D | 2-Way Meter - Electr | DAPjm | Islanded Distr. Cust. Storage | 2-Way Meter - Electr shall be able to process & send Meter out of capped kwh mode alert to DAPjm | meter_out_of_capped_kwh_mode_alert | alert | 24x7 | 1 per ¦ ElectrMtr per ¦ in-capped kwh mode cancel cmd | > 99% | < 5 sec | 50 - 150 | cmd |  | X | X | up |  | x | IDCS-095 |  |  | 0.041667 | 1 | ElectrMtr | fdrDCS-ElectrMtr | 5 | 5 | 150 | 1 | 2.3148e-09 | 5.787e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 2.3672e-09 | 5.9179e-06 | 0.085414 | 213.5351 | 0.085414 | 213.5351 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245992.4553 | 0.00056943 | 1.4236 | 0.00056943 | 1.4236 | 1.6647e-12 | 4.1617e-09 | 0.085414 | 213.5351 | 0.085414 | 213.5351 | 0.0028471 | 7.1178 | 0.0028471 | 7.1178
IDCS-x1 | c | 5Ba | DAPjm | ESI - In Meter | Islanded Distr. Cust. Storage | DAPjm shall be able to process & forward on_distr-cust-strg_alarm to ESI - In Meter | on_distr-cust-strg_alarm | alarm | 24x7 | 1 per ¦ ElectrMtr-with-Utl-joined-IPD-or-CustEMS per ¦ on-DCS-power event | > 98% | < 5 sec | 50 - 150 | event | N | X | X | down |  | x | IDCS- |  |  | 0.041667 | 2 | ElectrMtr | ElectrMtr-with-Utl-joined-IPD-or-CustEMS | 5 | 5 | 150 | 1 | 8.8359e-10 | 1.29e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 1.2322e-08 | 1.7991e-05 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 8.6654e-12 | 1.2652e-08 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382
IDCS-x2 | c | 5Ba | DAPjm | ESI - In Meter | Islanded Distr. Cust. Storage | DAPjm shall be able to process & forward off_distr-cust-strg_alert to ESI - In Meter | off_distr-cust-strg_alert | alert | 24x7 | 1 per ¦ ElectrMtr-with-Utl-joined-IPD-or-CustEMS per ¦ off-DCS-power event | > 98% | < 5 sec | 50 - 150 | event | N | X | X | down |  | x | IDCS- |  |  | 0.041667 | 2 | ElectrMtr | ElectrMtr-with-Utl-joined-IPD-or-CustEMS | 5 | 5 | 150 | 1 | 8.8359e-10 | 1.29e-06 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 1.2322e-08 | 1.7991e-05 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382 | [12 empty] | 0 |  | 0 | [12 empty] | 0 |  | 0 | 3354640 | 0.0029641 | 4.3276 | 0.0029641 | 4.3276 | 8.6654e-12 | 1.2652e-08 | 0.44462 | 649.1468 | 0.44462 | 649.1468 | 0.014821 | 21.6382 | 0.014821 | 21.6382
ME-002 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Events | 2-Way Meter - Electr shall send an audit/application event to the DAPjm | Audit_Application_Event | alert | 24x7 | 1 per 1000 per ¦ ElectrMtr per ¦ month | > 98% | < 1 min | 25 - 278 | month |  | X | X | up |  | x | ME-001 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 60 | 30 | 278 | 2 | 3.858e-10 | 3.858e-10 | 206400 | 7.963e-05 | 7.963e-05 | 0.00015926 | 0.00015926 | 6.1351e-10 | 6.1351e-10 | 0.022137 | 0.022137 | 0.041248 | 0.041248 | 0.0047778 | 0.0047778 | 0.0047778 | 0.0047778 | 615700 | 0.00023754 | 0.00023754 | 0.00047508 | 0.00047508 | 1.4711e-10 | 1.4711e-10 | 0.066036 | 0.066036 | 0.12304 | 0.12304 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 882800 | 0.00034059 | 0.00034059 | 0.00068117 | 0.00068117 | 2.6241e-09 | 2.6241e-09 | 0.094683 | 0.094683 | 0.17642 | 0.17642 | 0.020435 | 0.020435 | 0.020435 | 0.020435 | 485900 | 0.00018746 | 0.00018746 | 0.00037492 | 0.00037492 | 3.2314e-12 | 3.2314e-12 | 0.052114 | 0.052114 | 0.097105 | 0.097105 | 0.011248 | 0.011248 | 0.011248 | 0.011248 | 107700 | 4.1551e-05 | 4.1551e-05 | 8.3102e-05 | 8.3102e-05 | 2.2513e-13 | 2.2513e-13 | 0.011551 | 0.011551 | 0.021523 | 0.021523 | 0.0024931 | 0.0024931 | 0.0024931 | 0.0024931 | 2298500 | 0.00088677 | 0.00088677 | 0.0017735 | 0.0017735 | 4.8046e-12 | 4.8046e-12 | 0.24652 | 0.24652 | 0.45935 | 0.45935 | 0.053206 | 0.053206 | 0.053206 | 0.053206
ME-006 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Events | 2-Way Meter - Electr shall send configuration event to the DAPjm | Configuration_Event | alarm | 24x7 | 1 per 1000 per ¦ ElectrMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  |  | X | up |  | x | ME-005 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 30 | 15 | 278 | 2 |  | 1.1574e-05 | 206400 |  | 2.3889 |  | 4.7778 |  | 1.8405e-05 |  | 664.1111 |  | 1237.4444 |  | 71.6667 |  | 71.6667 | 615700 |  | 7.1262 |  | 14.2523 |  | 4.4132e-06 |  | 1981.0718 |  | 3691.3495 |  | 213.7847 |  | 213.7847 | 882800 |  | 10.2176 |  | 20.4352 |  | 7.8722e-05 |  | 2840.4907 |  | 5292.713 |  | 306.5278 |  | 306.5278 | 485900 |  | 5.6238 |  | 11.2477 |  | 9.6942e-08 |  | 1563.4282 |  | 2913.1505 |  | 168.7153 |  | 168.7153 | 107700 |  | 1.2465 |  | 2.4931 |  | 6.7538e-09 |  | 346.5347 |  | 645.7014 |  | 37.3958 |  | 37.3958 | 2298500 |  | 26.603 |  | 53.206 |  | 1.4414e-07 |  | 7395.6366 |  | 13780.3588 | 0 | 798.0903 | 0 | 798.0903
ME-010 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Events | 2-Way Meter - Electr shall send a fault/error/alarm event to the DAPjm | Fault_Error_Alarm_Event | alarm | 24x7 | 1 per 1000 per ¦ ElectrMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-009 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 206400 | 7.963e-05 | 7.963e-05 | 0.00015926 | 0.00015926 | 6.1351e-10 | 6.1351e-10 | 0.022137 | 0.022137 | 0.041248 | 0.041248 | 0.0023889 | 0.0023889 | 0.0023889 | 0.0023889 | 615700 | 0.00023754 | 0.00023754 | 0.00047508 | 0.00047508 | 1.4711e-10 | 1.4711e-10 | 0.066036 | 0.066036 | 0.12304 | 0.12304 | 0.0071262 | 0.0071262 | 0.0071262 | 0.0071262 | 882800 | 0.00034059 | 0.00034059 | 0.00068117 | 0.00068117 | 2.6241e-09 | 2.6241e-09 | 0.094683 | 0.094683 | 0.17642 | 0.17642 | 0.010218 | 0.010218 | 0.010218 | 0.010218 | 485900 | 0.00018746 | 0.00018746 | 0.00037492 | 0.00037492 | 3.2314e-12 | 3.2314e-12 | 0.052114 | 0.052114 | 0.097105 | 0.097105 | 0.0056238 | 0.0056238 | 0.0056238 | 0.0056238 | 107700 | 4.1551e-05 | 4.1551e-05 | 8.3102e-05 | 8.3102e-05 | 2.2513e-13 | 2.2513e-13 | 0.011551 | 0.011551 | 0.021523 | 0.021523 | 0.0012465 | 0.0012465 | 0.0012465 | 0.0012465 | 2298500 | 0.00088677 | 0.00088677 | 0.0017735 | 0.0017735 | 4.8046e-12 | 4.8046e-12 | 0.24652 | 0.24652 | 0.45935 | 0.45935 | 0.026603 | 0.026603 | 0.026603 | 0.026603
ME-014 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Events | 2-Way Meter - Electr shall send a power quality event to the DAPjm | Power_Quality_Event | alarm | 24x7 | 1 per 1000 per ¦ ElectrMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-013 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 206400 | 7.963e-05 | 7.963e-05 | 0.00015926 | 0.00015926 | 6.1351e-10 | 6.1351e-10 | 0.022137 | 0.022137 | 0.041248 | 0.041248 | 0.0023889 | 0.0023889 | 0.0023889 | 0.0023889 | 615700 | 0.00023754 | 0.00023754 | 0.00047508 | 0.00047508 | 1.4711e-10 | 1.4711e-10 | 0.066036 | 0.066036 | 0.12304 | 0.12304 | 0.0071262 | 0.0071262 | 0.0071262 | 0.0071262 | 882800 | 0.00034059 | 0.00034059 | 0.00068117 | 0.00068117 | 2.6241e-09 | 2.6241e-09 | 0.094683 | 0.094683 | 0.17642 | 0.17642 | 0.010218 | 0.010218 | 0.010218 | 0.010218 | 485900 | 0.00018746 | 0.00018746 | 0.00037492 | 0.00037492 | 3.2314e-12 | 3.2314e-12 | 0.052114 | 0.052114 | 0.097105 | 0.097105 | 0.0056238 | 0.0056238 | 0.0056238 | 0.0056238 | 107700 | 4.1551e-05 | 4.1551e-05 | 8.3102e-05 | 8.3102e-05 | 2.2513e-13 | 2.2513e-13 | 0.011551 | 0.011551 | 0.021523 | 0.021523 | 0.0012465 | 0.0012465 | 0.0012465 | 0.0012465 | 2298500 | 0.00088677 | 0.00088677 | 0.0017735 | 0.0017735 | 4.8046e-12 | 4.8046e-12 | 0.24652 | 0.24652 | 0.45935 | 0.45935 | 0.026603 | 0.026603 | 0.026603 | 0.026603
ME-018 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Events | 2-Way Meter - Electr shall send a security event to the DAPjm | Security_Event | alarm | 24x7 | 1 per 1000 per ¦ ElectrMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-017 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 206400 | 7.963e-05 | 7.963e-05 | 0.00015926 | 0.00015926 | 6.1351e-10 | 6.1351e-10 | 0.022137 | 0.022137 | 0.041248 | 0.041248 | 0.0023889 | 0.0023889 | 0.0023889 | 0.0023889 | 615700 | 0.00023754 | 0.00023754 | 0.00047508 | 0.00047508 | 1.4711e-10 | 1.4711e-10 | 0.066036 | 0.066036 | 0.12304 | 0.12304 | 0.0071262 | 0.0071262 | 0.0071262 | 0.0071262 | 882800 | 0.00034059 | 0.00034059 | 0.00068117 | 0.00068117 | 2.6241e-09 | 2.6241e-09 | 0.094683 | 0.094683 | 0.17642 | 0.17642 | 0.010218 | 0.010218 | 0.010218 | 0.010218 | 485900 | 0.00018746 | 0.00018746 | 0.00037492 | 0.00037492 | 3.2314e-12 | 3.2314e-12 | 0.052114 | 0.052114 | 0.097105 | 0.097105 | 0.0056238 | 0.0056238 | 0.0056238 | 0.0056238 | 107700 | 4.1551e-05 | 4.1551e-05 | 8.3102e-05 | 8.3102e-05 | 2.2513e-13 | 2.2513e-13 | 0.011551 | 0.011551 | 0.021523 | 0.021523 | 0.0012465 | 0.0012465 | 0.0012465 | 0.0012465 | 2298500 | 0.00088677 | 0.00088677 | 0.0017735 | 0.0017735 | 4.8046e-12 | 4.8046e-12 | 0.24652 | 0.24652 | 0.45935 | 0.45935 | 0.026603 | 0.026603 | 0.026603 | 0.026603
ME-025 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Events | 2-Way Meter - Gas shall be able to report & forward an audit/application event to DAPjm | Audit_Application_Event | alert | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ month | > 98% | < 1 min | 25 - 278 | month |  | X | X | up |  | x | ME-024 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 60 | 30 | 278 | 2 | 3.858e-10 | 3.858e-10 | 180200 | 6.9522e-05 | 6.9522e-05 | 0.00013904 | 0.00013904 | 5.3563e-10 | 5.3563e-10 | 0.019327 | 0.019327 | 0.036012 | 0.036012 | 0.0041713 | 0.0041713 | 0.0041713 | 0.0041713 | 544600 | 0.00021011 | 0.00021011 | 0.00042022 | 0.00042022 | 1.3012e-10 | 1.3012e-10 | 0.05841 | 0.05841 | 0.10884 | 0.10884 | 0.012606 | 0.012606 | 0.012606 | 0.012606 | 710300 | 0.00027404 | 0.00027404 | 0.00054807 | 0.00054807 | 2.1113e-09 | 2.1113e-09 | 0.076182 | 0.076182 | 0.14195 | 0.14195 | 0.016442 | 0.016442 | 0.016442 | 0.016442 | 275800 | 0.0001064 | 0.0001064 | 0.00021281 | 0.00021281 | 1.8342e-12 | 1.8342e-12 | 0.02958 | 0.02958 | 0.055117 | 0.055117 | 0.0063843 | 0.0063843 | 0.0063843 | 0.0063843 | 50900 | 1.9637e-05 | 1.9637e-05 | 3.9275e-05 | 3.9275e-05 | 1.064e-13 | 1.064e-13 | 0.0054592 | 0.0054592 | 0.010172 | 0.010172 | 0.0011782 | 0.0011782 | 0.0011782 | 0.0011782 | 1761800 | 0.00067971 | 0.00067971 | 0.0013594 | 0.0013594 | 3.6827e-12 | 3.6827e-12 | 0.18896 | 0.18896 | 0.35209 | 0.35209 | 0.040782 | 0.040782 | 0.040782 | 0.040782
ME-037 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Events | 2-Way Meter - Water shall be able to report & forward an audit/application event to DAPjm | Audit_Application_Event | alert | 24x7 | 1 per 1000 per ¦ WaterMtr per ¦ month | > 98% | < 1 min | 25 - 278 | month |  | X | X | up |  | x | ME-036 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 60 | 30 | 278 | 2 | 3.858e-10 | 3.858e-10 | 126200 | 4.8688e-05 | 4.8688e-05 | 9.7377e-05 | 9.7377e-05 | 3.7512e-10 | 3.7512e-10 | 0.013535 | 0.013535 | 0.025221 | 0.025221 | 0.0029213 | 0.0029213 | 0.0029213 | 0.0029213 | 383600 | 0.00014799 | 0.00014799 | 0.00029599 | 0.00029599 | 9.1653e-11 | 9.1653e-11 | 0.041142 | 0.041142 | 0.076661 | 0.076661 | 0.0088796 | 0.0088796 | 0.0088796 | 0.0088796 | 909500 | 0.00035089 | 0.00035089 | 0.00070177 | 0.00070177 | 2.7034e-09 | 2.7034e-09 | 0.097547 | 0.097547 | 0.18176 | 0.18176 | 0.021053 | 0.021053 | 0.021053 | 0.021053 | 279400 | 0.00010779 | 0.00010779 | 0.00021559 | 0.00021559 | 1.8581e-12 | 1.8581e-12 | 0.029967 | 0.029967 | 0.055837 | 0.055837 | 0.0064676 | 0.0064676 | 0.0064676 | 0.0064676 | 25600 | 9.8765e-06 | 9.8765e-06 | 1.9753e-05 | 1.9753e-05 | 5.3512e-14 | 5.3512e-14 | 0.0027457 | 0.0027457 | 0.005116 | 0.005116 | 0.00059259 | 0.00059259 | 0.00059259 | 0.00059259 | 1724300 | 0.00066524 | 0.00066524 | 0.0013305 | 0.0013305 | 3.6043e-12 | 3.6043e-12 | 0.18494 | 0.18494 | 0.34459 | 0.34459 | 0.039914 | 0.039914 | 0.039914 | 0.039914
ME-052 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Events | 2-Way Meter - Gas shall be able to report & forward configuration event to DAPjm | Configuration_Event | alarm | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ month | > 98% | < 1 min | 25 - 278 | month |  |  | X | up |  | x | ME-051 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 60 | 30 | 278 | 2 |  | 1.1574e-05 | 180200 |  | 2.0856 |  | 4.1713 |  | 1.6069e-05 |  | 579.8102 |  | 1080.3657 |  | 125.1389 |  | 125.1389 | 544600 |  | 6.3032 |  | 12.6065 |  | 3.9036e-06 |  | 1752.3009 |  | 3265.0787 |  | 378.1944 |  | 378.1944 | 710300 |  | 8.2211 |  | 16.4421 |  | 6.3339e-05 |  | 2285.456 |  | 4258.5116 |  | 493.2639 |  | 493.2639 | 275800 |  | 3.1921 |  | 6.3843 |  | 5.5025e-08 |  | 887.412 |  | 1653.5231 |  | 191.5278 |  | 191.5278 | 50900 |  | 0.58912 |  | 1.1782 |  | 3.1919e-09 |  | 163.7755 |  | 305.1644 |  | 35.3472 |  | 35.3472 | 1761800 |  | 20.3912 |  | 40.7824 |  | 1.1048e-07 |  | 5668.7546 |  | 10562.6435 | 0 | 1223.4722 | 0 | 1223.4722
ME-064 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Events | 2-Way Meter - Water shall be able to report & forward configuration event to DAPjm | Configuration_Event | alarm | 24x7 | 1 per 1000 per ¦ WaterMtr per ¦ month | > 98% | < 1 min | 25 - 278 | month |  |  | X | up |  | x | ME-063 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 60 | 30 | 278 | 2 |  | 1.1574e-05 | 126200 |  | 1.4606 |  | 2.9213 |  | 1.1254e-05 |  | 406.0602 |  | 756.6157 |  | 87.6389 |  | 87.6389 | 383600 |  | 4.4398 |  | 8.8796 |  | 2.7496e-06 |  | 1234.2685 |  | 2299.8241 |  | 266.3889 |  | 266.3889 | 909500 |  | 10.5266 |  | 21.0532 |  | 8.1103e-05 |  | 2926.4005 |  | 5452.7894 |  | 631.5972 |  | 631.5972 | 279400 |  | 3.2338 |  | 6.4676 |  | 5.5743e-08 |  | 898.9954 |  | 1675.1065 |  | 194.0278 |  | 194.0278 | 25600 |  | 0.2963 |  | 0.59259 |  | 1.6054e-09 |  | 82.3704 |  | 153.4815 |  | 17.7778 |  | 17.7778 | 1724300 |  | 19.9572 |  | 39.9144 |  | 1.0813e-07 |  | 5548.0949 |  | 10337.8171 | 0 | 1197.4306 | 0 | 1197.4306
ME-079 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Events | 2-Way Meter - Gas shall be able to report & forward a fault/error/alarm event to DAPjm | Fault_Error_Alarm_Event | alarm | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-078 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 180200 | 6.9522e-05 | 6.9522e-05 | 0.00013904 | 0.00013904 | 5.3563e-10 | 5.3563e-10 | 0.019327 | 0.019327 | 0.036012 | 0.036012 | 0.0020856 | 0.0020856 | 0.0020856 | 0.0020856 | 544600 | 0.00021011 | 0.00021011 | 0.00042022 | 0.00042022 | 1.3012e-10 | 1.3012e-10 | 0.05841 | 0.05841 | 0.10884 | 0.10884 | 0.0063032 | 0.0063032 | 0.0063032 | 0.0063032 | 710300 | 0.00027404 | 0.00027404 | 0.00054807 | 0.00054807 | 2.1113e-09 | 2.1113e-09 | 0.076182 | 0.076182 | 0.14195 | 0.14195 | 0.0082211 | 0.0082211 | 0.0082211 | 0.0082211 | 275800 | 0.0001064 | 0.0001064 | 0.00021281 | 0.00021281 | 1.8342e-12 | 1.8342e-12 | 0.02958 | 0.02958 | 0.055117 | 0.055117 | 0.0031921 | 0.0031921 | 0.0031921 | 0.0031921 | 50900 | 1.9637e-05 | 1.9637e-05 | 3.9275e-05 | 3.9275e-05 | 1.064e-13 | 1.064e-13 | 0.0054592 | 0.0054592 | 0.010172 | 0.010172 | 0.00058912 | 0.00058912 | 0.00058912 | 0.00058912 | 1761800 | 0.00067971 | 0.00067971 | 0.0013594 | 0.0013594 | 3.6827e-12 | 3.6827e-12 | 0.18896 | 0.18896 | 0.35209 | 0.35209 | 0.020391 | 0.020391 | 0.020391 | 0.020391
ME-091 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Events | 2-Way Meter - Water shall be able to report & forward a fault/error/alarm event to DAPjm | Fault_Error_Alarm_Event | alarm | 24x7 | 1 per 1000 per ¦ WaterMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-090 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 126200 | 4.8688e-05 | 4.8688e-05 | 9.7377e-05 | 9.7377e-05 | 3.7512e-10 | 3.7512e-10 | 0.013535 | 0.013535 | 0.025221 | 0.025221 | 0.0014606 | 0.0014606 | 0.0014606 | 0.0014606 | 383600 | 0.00014799 | 0.00014799 | 0.00029599 | 0.00029599 | 9.1653e-11 | 9.1653e-11 | 0.041142 | 0.041142 | 0.076661 | 0.076661 | 0.0044398 | 0.0044398 | 0.0044398 | 0.0044398 | 909500 | 0.00035089 | 0.00035089 | 0.00070177 | 0.00070177 | 2.7034e-09 | 2.7034e-09 | 0.097547 | 0.097547 | 0.18176 | 0.18176 | 0.010527 | 0.010527 | 0.010527 | 0.010527 | 279400 | 0.00010779 | 0.00010779 | 0.00021559 | 0.00021559 | 1.8581e-12 | 1.8581e-12 | 0.029967 | 0.029967 | 0.055837 | 0.055837 | 0.0032338 | 0.0032338 | 0.0032338 | 0.0032338 | 25600 | 9.8765e-06 | 9.8765e-06 | 1.9753e-05 | 1.9753e-05 | 5.3512e-14 | 5.3512e-14 | 0.0027457 | 0.0027457 | 0.005116 | 0.005116 | 0.0002963 | 0.0002963 | 0.0002963 | 0.0002963 | 1724300 | 0.00066524 | 0.00066524 | 0.0013305 | 0.0013305 | 3.6043e-12 | 3.6043e-12 | 0.18494 | 0.18494 | 0.34459 | 0.34459 | 0.019957 | 0.019957 | 0.019957 | 0.019957
ME-109 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Events | 2-Way Meter - Gas shall be able to report & forward a security event to DAPjm | Security_Event | alarm | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-108 |  |  | 0.041667 | 1 | GasMtr | GasMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 180200 | 6.9522e-05 | 6.9522e-05 | 0.00013904 | 0.00013904 | 5.3563e-10 | 5.3563e-10 | 0.019327 | 0.019327 | 0.036012 | 0.036012 | 0.0020856 | 0.0020856 | 0.0020856 | 0.0020856 | 544600 | 0.00021011 | 0.00021011 | 0.00042022 | 0.00042022 | 1.3012e-10 | 1.3012e-10 | 0.05841 | 0.05841 | 0.10884 | 0.10884 | 0.0063032 | 0.0063032 | 0.0063032 | 0.0063032 | 710300 | 0.00027404 | 0.00027404 | 0.00054807 | 0.00054807 | 2.1113e-09 | 2.1113e-09 | 0.076182 | 0.076182 | 0.14195 | 0.14195 | 0.0082211 | 0.0082211 | 0.0082211 | 0.0082211 | 275800 | 0.0001064 | 0.0001064 | 0.00021281 | 0.00021281 | 1.8342e-12 | 1.8342e-12 | 0.02958 | 0.02958 | 0.055117 | 0.055117 | 0.0031921 | 0.0031921 | 0.0031921 | 0.0031921 | 50900 | 1.9637e-05 | 1.9637e-05 | 3.9275e-05 | 3.9275e-05 | 1.064e-13 | 1.064e-13 | 0.0054592 | 0.0054592 | 0.010172 | 0.010172 | 0.00058912 | 0.00058912 | 0.00058912 | 0.00058912 | 1761800 | 0.00067971 | 0.00067971 | 0.0013594 | 0.0013594 | 3.6827e-12 | 3.6827e-12 | 0.18896 | 0.18896 | 0.35209 | 0.35209 | 0.020391 | 0.020391 | 0.020391 | 0.020391
ME-121 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Events | 2-Way Meter - Water shall be able to report & forward a security event to DAPjm | Security_Event | alarm | 24x7 | 1 per 1000 per ¦ WaterMtr per ¦ month | > 98% | < 30 sec | 25 - 278 | month |  | X | X | up |  | x | ME-120 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 30 | 15 | 278 | 2 | 3.858e-10 | 3.858e-10 | 126200 | 4.8688e-05 | 4.8688e-05 | 9.7377e-05 | 9.7377e-05 | 3.7512e-10 | 3.7512e-10 | 0.013535 | 0.013535 | 0.025221 | 0.025221 | 0.0014606 | 0.0014606 | 0.0014606 | 0.0014606 | 383600 | 0.00014799 | 0.00014799 | 0.00029599 | 0.00029599 | 9.1653e-11 | 9.1653e-11 | 0.041142 | 0.041142 | 0.076661 | 0.076661 | 0.0044398 | 0.0044398 | 0.0044398 | 0.0044398 | 909500 | 0.00035089 | 0.00035089 | 0.00070177 | 0.00070177 | 2.7034e-09 | 2.7034e-09 | 0.097547 | 0.097547 | 0.18176 | 0.18176 | 0.010527 | 0.010527 | 0.010527 | 0.010527 | 279400 | 0.00010779 | 0.00010779 | 0.00021559 | 0.00021559 | 1.8581e-12 | 1.8581e-12 | 0.029967 | 0.029967 | 0.055837 | 0.055837 | 0.0032338 | 0.0032338 | 0.0032338 | 0.0032338 | 25600 | 9.8765e-06 | 9.8765e-06 | 1.9753e-05 | 1.9753e-05 | 5.3512e-14 | 5.3512e-14 | 0.0027457 | 0.0027457 | 0.005116 | 0.005116 | 0.0002963 | 0.0002963 | 0.0002963 | 0.0002963 | 1724300 | 0.00066524 | 0.00066524 | 0.0013305 | 0.0013305 | 3.6043e-12 | 3.6043e-12 | 0.18494 | 0.18494 | 0.34459 | 0.34459 | 0.019957 | 0.019957 | 0.019957 | 0.019957
MR-025 | c | 1D | DAPjm | 2-Way Meter - Electr | Meter Reading | DAPjm may be able to forward multiple interval meter reading request to 2-Way Meter - Electr | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | down |  | x | MR-007 |  |  | 0.090909 | 1 | ElectrMtr | ElectrMtr | 5 | 5 | 25 | 1 | 6.3131e-07 | 6.3131e-07 | 206400 | 0.1303 | 0.1303 | 0.1303 | 0.1303 | 9.0281e-08 | 9.0281e-08 | 3.2576 | 3.2576 | 3.2576 | 3.2576 | 0.65152 | 0.65152 | 0.65152 | 0.65152 | 615700 | 0.3887 | 0.3887 | 0.3887 | 0.3887 | 2.1648e-08 | 2.1648e-08 | 9.7175 | 9.7175 | 9.7175 | 9.7175 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 882800 | 0.55732 | 0.55732 | 0.55732 | 0.55732 | 3.8614e-07 | 3.8614e-07 | 13.9331 | 13.9331 | 13.9331 | 13.9331 | 2.7866 | 2.7866 | 2.7866 | 2.7866 | 485900 | 0.30676 | 0.30676 | 0.30676 | 0.30676 | 4.7552e-10 | 4.7552e-10 | 7.6689 | 7.6689 | 7.6689 | 7.6689 | 1.5338 | 1.5338 | 1.5338 | 1.5338 | 107700 | 0.067992 | 0.067992 | 0.067992 | 0.067992 | 3.3128e-11 | 3.3128e-11 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 0.33996 | 0.33996 | 0.33996 | 0.33996 | 2298500 | 1.4511 | 1.4511 | 1.4511 | 1.4511 | 7.0702e-10 | 7.0702e-10 | 36.2768 | 36.2768 | 36.2768 | 36.2768 | 7.2554 | 7.2554 | 7.2554 | 7.2554
MR-027 | c | 1D | DAPjm | 2-Way Meter - Electr | Meter Reading | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Electr | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | down |  | x | MR-002 |  |  | 0.066667 | 1 | ElectrMtr | ElectrMtr | 5 | 5 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 206400 | 0.095556 | 0.095556 | 0.095556 | 0.095556 | 6.6206e-08 | 6.6206e-08 | 2.3889 | 2.3889 | 2.3889 | 2.3889 | 0.47778 | 0.47778 | 0.47778 | 0.47778 | 615700 | 0.28505 | 0.28505 | 0.28505 | 0.28505 | 1.5875e-08 | 1.5875e-08 | 7.1262 | 7.1262 | 7.1262 | 7.1262 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 882800 | 0.4087 | 0.4087 | 0.4087 | 0.4087 | 2.8317e-07 | 2.8317e-07 | 10.2176 | 10.2176 | 10.2176 | 10.2176 | 2.0435 | 2.0435 | 2.0435 | 2.0435 | 485900 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 3.4871e-10 | 3.4871e-10 | 5.6238 | 5.6238 | 5.6238 | 5.6238 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 107700 | 0.049861 | 0.049861 | 0.049861 | 0.049861 | 2.4294e-11 | 2.4294e-11 | 1.2465 | 1.2465 | 1.2465 | 1.2465 | 0.24931 | 0.24931 | 0.24931 | 0.24931 | 2298500 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 5.1848e-10 | 5.1848e-10 | 26.603 | 26.603 | 26.603 | 26.603 | 5.3206 | 5.3206 | 5.3206 | 5.3206
MR-032 | c | 1Dg | 2-Way Meter - Gas C/I | DAPjm | Meter Reading | 2-Way Meter - Gas C/I shall be able to send multi interval-data meter reads data to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 per ¦ GasC/IMtr per ¦ day (may have 15 min vs 1hr interval data) | 90% success every 4-6 hr, 98% success over 1 day, > 99.5% over 2 day | < 4 hr (expected window of data delivery) | 1600 for 4hr of data - 2400 for 6hr of data | day |  | X | X | up |  | x | MR-036 |  |  | 0.041667 | 1 | GasC/IMtr | GasC/IMtr | 9600 | 1371.4286 | 1600 | 7 | 6.9444e-05 | 6.9444e-05 | 45200 | 3.1389 | 3.1389 | 21.9722 | 21.9722 | 0.00013919 | 0.00013919 | 5022.2222 | 5022.2222 | 5690.8056 | 5690.8056 | 30133.3333 | 30133.3333 | 30133.3333 | 30133.3333 | 142100 | 9.8681 | 9.8681 | 69.0764 | 69.0764 | 3.5173e-05 | 3.5173e-05 | 15788.8889 | 15788.8889 | 17890.7847 | 17890.7847 | 94733.3333 | 94733.3333 | 94733.3333 | 94733.3333 | 117000 | 8.125 | 8.125 | 56.875 | 56.875 | 0.00036028 | 0.00036028 | 13000 | 13000 | 14730.625 | 14730.625 | 78000 | 78000 | 78000 | 78000 | 69300 | 4.8125 | 4.8125 | 33.6875 | 33.6875 | 4.7745e-07 | 4.7745e-07 | 7700 | 7700 | 8725.0625 | 8725.0625 | 46200 | 46200 | 46200 | 46200 | 18200 | 1.2639 | 1.2639 | 8.8472 | 8.8472 | 3.9412e-08 | 3.9412e-08 | 2022.2222 | 2022.2222 | 2291.4306 | 2291.4306 | 12133.3333 | 12133.3333 | 12133.3333 | 12133.3333 | 391800 | 27.2083 | 27.2083 | 190.4583 | 190.4583 | 8.4844e-07 | 8.4844e-07 | 43533.3333 | 43533.3333 | 49328.7083 | 49328.7083 | 261200 | 261200 | 261200 | 261200
MR-033 | c | 1Dg | 2-Way Meter - Gas Resdnt | DAPjm | Meter Reading | 2-Way Meter - Gas Resdnt shall be able to send multi interval-data meter reads data to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 1-6 per ¦ GasResdntMtr per ¦ day (with 4hr -24h interval data) | 90% success every 4-6 hr, 98% success over 1 day, > 99.5% over 2 day | < 4 hr (expected window of data delivery) | 1600 for 4hr of data - 2400 for 6hr of data | day |  | X | X | up |  | x | MR-037 |  |  | 0.041667 | 1 | GasMtr | GasResdntMtr | 9600 | 1371.4286 | 1600 | 7 | 6.9444e-05 | 6.9444e-05 | 135000 | 9.375 | 9.375 | 65.625 | 65.625 | 0.00041571 | 0.00041571 | 15000 | 15000 | 16996.875 | 16996.875 | 90000 | 90000 | 90000 | 90000 | 402500 | 27.9514 | 27.9514 | 195.6597 | 195.6597 | 9.9628e-05 | 9.9628e-05 | 44722.2222 | 44722.2222 | 50675.8681 | 50675.8681 | 268333.3333 | 268333.3333 | 268333.3333 | 268333.3333 | 593300 | 41.2014 | 41.2014 | 288.4097 | 288.4097 | 0.001827 | 0.001827 | 65922.2222 | 65922.2222 | 74698.1181 | 74698.1181 | 395533.3333 | 395533.3333 | 395533.3333 | 395533.3333 | 206500 | 14.3403 | 14.3403 | 100.3819 | 100.3819 | 1.4227e-06 | 1.4227e-06 | 22944.4444 | 22944.4444 | 25998.9236 | 25998.9236 | 137666.6667 | 137666.6667 | 137666.6667 | 137666.6667 | 32700 | 2.2708 | 2.2708 | 15.8958 | 15.8958 | 7.0812e-08 | 7.0812e-08 | 3633.3333 | 3633.3333 | 4117.0208 | 4117.0208 | 21800 | 21800 | 21800 | 21800 | 1370000 | 95.1389 | 95.1389 | 665.9722 | 665.9722 | 2.9667e-06 | 2.9667e-06 | 152222.2222 | 152222.2222 | 172486.8056 | 172486.8056 | 913333.3333 | 913333.3333 | 913333.3333 | 913333.3333
MR-034 | c | 1D | 2-Way Meter - Electr C/I | DAPjm | Meter Reading | 2-Way Meter - Electr C/I shall be able to send multi interval-data meter reads data to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 per ¦ ElectrC/IMtr per ¦ day (Intervals of 15 min to 1hr, 4-20 data points per interval) | > 98% success every 2 hr, > 99.5% success over 2 day, > 99.5% over 2 day | < 2 hr (expected window of data delivery) | 200 for 1hr interval 4 pts every hr - 1600 for 15 min interval 20 pts for 2 hr of data | day |  | X | X | up |  | x | MR-038 |  |  | 0.041667 | 1 | ElectrC/IMtr | ElectrC/IMtr | 7200 | 1028.5714 | 1600 | 7 | 6.9444e-05 | 6.9444e-05 | 71400 | 4.9583 | 4.9583 | 34.7083 | 34.7083 | 0.00021987 | 0.00021987 | 7933.3333 | 7933.3333 | 8989.4583 | 8989.4583 | 35700 | 35700 | 35700 | 35700 | 213200 | 14.8056 | 14.8056 | 103.6389 | 103.6389 | 5.2772e-05 | 5.2772e-05 | 23688.8889 | 23688.8889 | 26842.4722 | 26842.4722 | 106600 | 106600 | 106600 | 106600 | 184800 | 12.8333 | 12.8333 | 89.8333 | 89.8333 | 0.00056906 | 0.00056906 | 20533.3333 | 20533.3333 | 23266.8333 | 23266.8333 | 92400 | 92400 | 92400 | 92400 | 72900 | 5.0625 | 5.0625 | 35.4375 | 35.4375 | 5.0225e-07 | 5.0225e-07 | 8100 | 8100 | 9178.3125 | 9178.3125 | 36450 | 36450 | 36450 | 36450 | 9600 | 0.66667 | 0.66667 | 4.6667 | 4.6667 | 2.0789e-08 | 2.0789e-08 | 1066.6667 | 1066.6667 | 1208.6667 | 1208.6667 | 4800 | 4800 | 4800 | 4800 | 551900 | 38.3264 | 38.3264 | 268.2847 | 268.2847 | 1.1951e-06 | 1.1951e-06 | 61322.2222 | 61322.2222 | 69485.7431 | 69485.7431 | 275950 | 275950 | 275950 | 275950
MR-035 | c | 1D | 2-Way Meter - Electr Resdnt | DAPjm | Meter Reading | 2-Way Meter - Electr Resdnt shall be able to send multi interval-data meter reads data to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 24x7 | 4-6 per ¦ ElectrResdIMtr per ¦ day (Intervals of 15 min to 1hr, 4-8 data points per interval) | 90% success every 4-6 hr, 98% success over 1 day, > 99.5% over 2 day | < 4 hr (expected window of data delivery) | 1600 for 4hr of data - 2400 for 6hr of data | day |  | X | X | up |  | x | MR-039 |  |  | 0.041667 | 1 | ElectrMtr | ElectrResdIMtr | 9600 | 1371.4286 | 1600 | 7 | 6.9444e-05 | 6.9444e-05 | 135000 | 9.375 | 9.375 | 65.625 | 65.625 | 0.00041571 | 0.00041571 | 15000 | 15000 | 16996.875 | 16996.875 | 90000 | 90000 | 90000 | 90000 | 402500 | 27.9514 | 27.9514 | 195.6597 | 195.6597 | 9.9628e-05 | 9.9628e-05 | 44722.2222 | 44722.2222 | 50675.8681 | 50675.8681 | 268333.3333 | 268333.3333 | 268333.3333 | 268333.3333 | 698000 | 48.4722 | 48.4722 | 339.3056 | 339.3056 | 0.0021494 | 0.0021494 | 77555.5556 | 77555.5556 | 87880.1389 | 87880.1389 | 465333.3333 | 465333.3333 | 465333.3333 | 465333.3333 | 413000 | 28.6806 | 28.6806 | 200.7639 | 200.7639 | 2.8454e-06 | 2.8454e-06 | 45888.8889 | 45888.8889 | 51997.8472 | 51997.8472 | 275333.3333 | 275333.3333 | 275333.3333 | 275333.3333 | 98100 | 6.8125 | 6.8125 | 47.6875 | 47.6875 | 2.1243e-07 | 2.1243e-07 | 10900 | 10900 | 12351.0625 | 12351.0625 | 65400 | 65400 | 65400 | 65400 | 1746600 | 121.2917 | 121.2917 | 849.0417 | 849.0417 | 3.7823e-06 | 3.7823e-06 | 194066.6667 | 194066.6667 | 219901.7917 | 219901.7917 | 1164400 | 1164400 | 1164400 | 1164400
MR-042 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Reading | 2-Way Meter - Electr shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ ElectrMtr per ¦ x on-demand Mtr read cmd | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | MR-043 |  |  | 0.066667 | 1 | ElectrMtr | ElectrMtr | 5 | 5 | 50 | 1 | 1.8519e-05 | 1.8519e-05 | 206400 | 3.8222 | 3.8222 | 3.8222 | 3.8222 | 5.2965e-06 | 5.2965e-06 | 191.1111 | 191.1111 | 191.1111 | 191.1111 | 19.1111 | 19.1111 | 19.1111 | 19.1111 | 615700 | 11.4019 | 11.4019 | 11.4019 | 11.4019 | 1.27e-06 | 1.27e-06 | 570.0926 | 570.0926 | 570.0926 | 570.0926 | 57.0093 | 57.0093 | 57.0093 | 57.0093 | 882800 | 16.3481 | 16.3481 | 16.3481 | 16.3481 | 2.2654e-05 | 2.2654e-05 | 817.4074 | 817.4074 | 817.4074 | 817.4074 | 81.7407 | 81.7407 | 81.7407 | 81.7407 | 485900 | 8.9981 | 8.9981 | 8.9981 | 8.9981 | 2.7897e-08 | 2.7897e-08 | 449.9074 | 449.9074 | 449.9074 | 449.9074 | 44.9907 | 44.9907 | 44.9907 | 44.9907 | 107700 | 1.9944 | 1.9944 | 1.9944 | 1.9944 | 1.9435e-09 | 1.9435e-09 | 99.7222 | 99.7222 | 99.7222 | 99.7222 | 9.9722 | 9.9722 | 9.9722 | 9.9722 | 2298500 | 42.5648 | 42.5648 | 42.5648 | 42.5648 | 4.1478e-08 | 4.1478e-08 | 2128.2407 | 2128.2407 | 2128.2407 | 2128.2407 | 212.8241 | 212.8241 | 212.8241 | 212.8241
MR-044 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Reading | 2-Way Meter - Electr shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | MR-045 |  |  | 0.066667 | 1 | ElectrMtr | ElectrMtr | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 206400 | 0.095556 | 0.095556 | 0.095556 | 0.095556 | 2.6482e-07 | 2.6482e-07 | 9.5556 | 9.5556 | 9.5556 | 9.5556 | 0.47778 | 0.47778 | 0.47778 | 0.47778 | 615700 | 0.28505 | 0.28505 | 0.28505 | 0.28505 | 6.35e-08 | 6.35e-08 | 28.5046 | 28.5046 | 28.5046 | 28.5046 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 882800 | 0.4087 | 0.4087 | 0.4087 | 0.4087 | 1.1327e-06 | 1.1327e-06 | 40.8704 | 40.8704 | 40.8704 | 40.8704 | 2.0435 | 2.0435 | 2.0435 | 2.0435 | 485900 | 0.22495 | 0.22495 | 0.22495 | 0.22495 | 1.3948e-09 | 1.3948e-09 | 22.4954 | 22.4954 | 22.4954 | 22.4954 | 1.1248 | 1.1248 | 1.1248 | 1.1248 | 107700 | 0.049861 | 0.049861 | 0.049861 | 0.049861 | 9.7177e-11 | 9.7177e-11 | 4.9861 | 4.9861 | 4.9861 | 4.9861 | 0.24931 | 0.24931 | 0.24931 | 0.24931 | 2298500 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 2.0739e-09 | 2.0739e-09 | 106.412 | 106.412 | 106.412 | 106.412 | 5.3206 | 5.3206 | 5.3206 | 5.3206
MR-115 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Reading | 2-Way Meter - Water shall be able to send meter read data to DAPjm | Mtr-read_data_resp-data | resp-data | 24x7 | 1 per ¦ WaterMtr per ¦ day | 98% success over 1 day, > 99.5% over 2 day | < 4 hr (expected window of data delivery) | 200 | day |  | X | X | up |  | x | MR-114 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr | 9600 | 9600 | 200 | 1 | 1.1574e-05 | 1.1574e-05 | 126200 | 1.4606 | 1.4606 | 1.4606 | 1.4606 | 8.0961e-06 | 8.0961e-06 | 292.1296 | 292.1296 | 292.1296 | 292.1296 | 14022.2222 | 14022.2222 | 14022.2222 | 14022.2222 | 383600 | 4.4398 | 4.4398 | 4.4398 | 4.4398 | 1.9781e-06 | 1.9781e-06 | 887.963 | 887.963 | 887.963 | 887.963 | 42622.2222 | 42622.2222 | 42622.2222 | 42622.2222 | 909500 | 10.5266 | 10.5266 | 10.5266 | 10.5266 | 5.8347e-05 | 5.8347e-05 | 2105.3241 | 2105.3241 | 2105.3241 | 2105.3241 | 101055.5556 | 101055.5556 | 101055.5556 | 101055.5556 | 279400 | 3.2338 | 3.2338 | 3.2338 | 3.2338 | 4.0103e-08 | 4.0103e-08 | 646.7593 | 646.7593 | 646.7593 | 646.7593 | 31044.4444 | 31044.4444 | 31044.4444 | 31044.4444 | 25600 | 0.2963 | 0.2963 | 0.2963 | 0.2963 | 1.1549e-09 | 1.1549e-09 | 59.2593 | 59.2593 | 59.2593 | 59.2593 | 2844.4444 | 2844.4444 | 2844.4444 | 2844.4444 | 1724300 | 19.9572 | 19.9572 | 19.9572 | 19.9572 | 7.7791e-08 | 7.7791e-08 | 3991.4352 | 3991.4352 | 3991.4352 | 3991.4352 | 191588.8889 | 191588.8889 | 191588.8889 | 191588.8889
MR-130 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Meter Reading | DAPjm may be able to forward multiple interval meter reading request to 2-Way Meter - Gas | Mtr-read_multi-interval-data_cmd | cmd | 7AM - 6PM | 25 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 1 hr | 25 | day |  | X | X | down |  | x | MR-124 |  |  | 0.090909 | 1 | GasMtr | GasMtr | 3600 | 3600 | 25 | 1 | 6.3131e-07 | 6.3131e-07 | 180200 | 0.11376 | 0.11376 | 0.11376 | 0.11376 | 7.8821e-08 | 7.8821e-08 | 2.8441 | 2.8441 | 2.8441 | 2.8441 | 409.5455 | 409.5455 | 409.5455 | 409.5455 | 544600 | 0.34381 | 0.34381 | 0.34381 | 0.34381 | 1.9148e-08 | 1.9148e-08 | 8.5953 | 8.5953 | 8.5953 | 8.5953 | 1237.7273 | 1237.7273 | 1237.7273 | 1237.7273 | 710300 | 0.44842 | 0.44842 | 0.44842 | 0.44842 | 3.1069e-07 | 3.1069e-07 | 11.2105 | 11.2105 | 11.2105 | 11.2105 | 1614.3182 | 1614.3182 | 1614.3182 | 1614.3182 | 275800 | 0.17412 | 0.17412 | 0.17412 | 0.17412 | 2.6991e-10 | 2.6991e-10 | 4.3529 | 4.3529 | 4.3529 | 4.3529 | 626.8182 | 626.8182 | 626.8182 | 626.8182 | 50900 | 0.032134 | 0.032134 | 0.032134 | 0.032134 | 1.5657e-11 | 1.5657e-11 | 0.80335 | 0.80335 | 0.80335 | 0.80335 | 115.6818 | 115.6818 | 115.6818 | 115.6818 | 1761800 | 1.1122 | 1.1122 | 1.1122 | 1.1122 | 5.4193e-10 | 5.4193e-10 | 27.8062 | 27.8062 | 27.8062 | 27.8062 | 4004.0909 | 4004.0909 | 4004.0909 | 4004.0909
MR-135 | c | 1D | 2-Way Meter - Electr | DAPjm | Meter Reading | 2-Way Meter - Electr shall be able to send multiple interval meter reading data (per specific meter request from MDMS) to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 5 sec | 200 - 2400 | day |  | X | X | up |  | x | MR-015 |  |  | 0.090909 | 1 | ElectrMtr | ElectrMtr | 5 | 0.5 | 2400 | 10 | 6.3131e-07 | 6.3131e-07 | 206400 | 0.1303 | 0.1303 | 1.303 | 1.303 | 8.667e-06 | 8.667e-06 | 312.7273 | 312.7273 | 337.4848 | 337.4848 | 0.65152 | 0.65152 | 0.65152 | 0.65152 | 615700 | 0.3887 | 0.3887 | 3.887 | 3.887 | 2.0782e-06 | 2.0782e-06 | 932.8788 | 932.8788 | 1006.7317 | 1006.7317 | 1.9435 | 1.9435 | 1.9435 | 1.9435 | 882800 | 0.55732 | 0.55732 | 5.5732 | 5.5732 | 3.707e-05 | 3.707e-05 | 1337.5758 | 1337.5758 | 1443.4672 | 1443.4672 | 2.7866 | 2.7866 | 2.7866 | 2.7866 | 485900 | 0.30676 | 0.30676 | 3.0676 | 3.0676 | 4.565e-08 | 4.565e-08 | 736.2121 | 736.2121 | 794.4956 | 794.4956 | 1.5338 | 1.5338 | 1.5338 | 1.5338 | 107700 | 0.067992 | 0.067992 | 0.67992 | 0.67992 | 3.1803e-09 | 3.1803e-09 | 163.1818 | 163.1818 | 176.1004 | 176.1004 | 0.33996 | 0.33996 | 0.33996 | 0.33996 | 2298500 | 1.4511 | 1.4511 | 14.5107 | 14.5107 | 6.7873e-08 | 6.7873e-08 | 3482.5758 | 3482.5758 | 3758.2797 | 3758.2797 | 7.2554 | 7.2554 | 7.2554 | 7.2554
MR-142 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Reading | 2-Way Meter - Gas shall be able to send multiple interval meter reading data (per specific meter request from MDMS) to DAPjm | Mtr-read_multi-interval-data_resp-data | resp-data | 7AM - 6PM | 25 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 5 sec | 200 - 2400 | day |  | X | X | up |  | x | MR-141 |  |  | 0.090909 | 1 | GasMtr | GasMtr | 5 | 0.5 | 2400 | 10 | 6.3131e-07 | 6.3131e-07 | 180200 | 0.11376 | 0.11376 | 1.1376 | 1.1376 | 7.5668e-06 | 7.5668e-06 | 273.0303 | 273.0303 | 294.6452 | 294.6452 | 0.56881 | 0.56881 | 0.56881 | 0.56881 | 544600 | 0.34381 | 0.34381 | 3.4381 | 3.4381 | 1.8382e-06 | 1.8382e-06 | 825.1515 | 825.1515 | 890.476 | 890.476 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 710300 | 0.44842 | 0.44842 | 4.4842 | 4.4842 | 2.9826e-05 | 2.9826e-05 | 1076.2121 | 1076.2121 | 1161.4122 | 1161.4122 | 2.2421 | 2.2421 | 2.2421 | 2.2421 | 275800 | 0.17412 | 0.17412 | 1.7412 | 1.7412 | 2.5911e-08 | 2.5911e-08 | 417.8788 | 417.8788 | 450.9609 | 450.9609 | 0.87058 | 0.87058 | 0.87058 | 0.87058 | 50900 | 0.032134 | 0.032134 | 0.32134 | 0.32134 | 1.503e-09 | 1.503e-09 | 77.1212 | 77.1212 | 83.2266 | 83.2266 | 0.16067 | 0.16067 | 0.16067 | 0.16067 | 1761800 | 1.1122 | 1.1122 | 11.1225 | 11.1225 | 5.2025e-08 | 5.2025e-08 | 2669.3939 | 2669.3939 | 2880.721 | 2880.721 | 5.5612 | 5.5612 | 5.5612 | 5.5612
MR-160 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Meter Reading | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Gas | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | down |  | x | MR-152 |  |  | 0.066667 | 1 | GasMtr | GasMtr | 5 | 5 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 180200 | 0.083426 | 0.083426 | 0.083426 | 0.083426 | 5.7802e-08 | 5.7802e-08 | 2.0856 | 2.0856 | 2.0856 | 2.0856 | 0.41713 | 0.41713 | 0.41713 | 0.41713 | 544600 | 0.25213 | 0.25213 | 0.25213 | 0.25213 | 1.4042e-08 | 1.4042e-08 | 6.3032 | 6.3032 | 6.3032 | 6.3032 | 1.2606 | 1.2606 | 1.2606 | 1.2606 | 710300 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 2.2784e-07 | 2.2784e-07 | 8.2211 | 8.2211 | 8.2211 | 8.2211 | 1.6442 | 1.6442 | 1.6442 | 1.6442 | 275800 | 0.12769 | 0.12769 | 0.12769 | 0.12769 | 1.9793e-10 | 1.9793e-10 | 3.1921 | 3.1921 | 3.1921 | 3.1921 | 0.63843 | 0.63843 | 0.63843 | 0.63843 | 50900 | 0.023565 | 0.023565 | 0.023565 | 0.023565 | 1.1482e-11 | 1.1482e-11 | 0.58912 | 0.58912 | 0.58912 | 0.58912 | 0.11782 | 0.11782 | 0.11782 | 0.11782 | 1761800 | 0.81565 | 0.81565 | 0.81565 | 0.81565 | 3.9741e-10 | 3.9741e-10 | 20.3912 | 20.3912 | 20.3912 | 20.3912 | 4.0782 | 4.0782 | 4.0782 | 4.0782
MR-173 | c | 1Dw | DAPjm | 2-Way Meter - Water | Meter Reading | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Water | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ WaterMtr per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | down |  | x | MR-165 |  |  | 0.066667 | 1 | WaterMtr | WaterMtr | 5 | 5 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 126200 | 0.058426 | 0.058426 | 0.058426 | 0.058426 | 4.0481e-08 | 4.0481e-08 | 1.4606 | 1.4606 | 1.4606 | 1.4606 | 0.29213 | 0.29213 | 0.29213 | 0.29213 | 383600 | 0.17759 | 0.17759 | 0.17759 | 0.17759 | 9.8906e-09 | 9.8906e-09 | 4.4398 | 4.4398 | 4.4398 | 4.4398 | 0.88796 | 0.88796 | 0.88796 | 0.88796 | 909500 | 0.42106 | 0.42106 | 0.42106 | 0.42106 | 2.9174e-07 | 2.9174e-07 | 10.5266 | 10.5266 | 10.5266 | 10.5266 | 2.1053 | 2.1053 | 2.1053 | 2.1053 | 279400 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 2.0051e-10 | 2.0051e-10 | 3.2338 | 3.2338 | 3.2338 | 3.2338 | 0.64676 | 0.64676 | 0.64676 | 0.64676 | 25600 | 0.011852 | 0.011852 | 0.011852 | 0.011852 | 5.7747e-12 | 5.7747e-12 | 0.2963 | 0.2963 | 0.2963 | 0.2963 | 0.059259 | 0.059259 | 0.059259 | 0.059259 | 1724300 | 0.79829 | 0.79829 | 0.79829 | 0.79829 | 3.8895e-10 | 3.8895e-10 | 19.9572 | 19.9572 | 19.9572 | 19.9572 | 3.9914 | 3.9914 | 3.9914 | 3.9914
MR-199 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Reading | 2-Way Meter - Gas shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ GasMtr per ¦ x on-demand Mtr read cmd | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | MR-198 |  |  | 0.066667 | 1 | GasMtr | GasMtr | 5 | 5 | 50 | 1 | 1.8519e-05 | 1.8519e-05 | 180200 | 3.337 | 3.337 | 3.337 | 3.337 | 4.6242e-06 | 4.6242e-06 | 166.8519 | 166.8519 | 166.8519 | 166.8519 | 16.6852 | 16.6852 | 16.6852 | 16.6852 | 544600 | 10.0852 | 10.0852 | 10.0852 | 10.0852 | 1.1233e-06 | 1.1233e-06 | 504.2593 | 504.2593 | 504.2593 | 504.2593 | 50.4259 | 50.4259 | 50.4259 | 50.4259 | 710300 | 13.1537 | 13.1537 | 13.1537 | 13.1537 | 1.8227e-05 | 1.8227e-05 | 657.6852 | 657.6852 | 657.6852 | 657.6852 | 65.7685 | 65.7685 | 65.7685 | 65.7685 | 275800 | 5.1074 | 5.1074 | 5.1074 | 5.1074 | 1.5834e-08 | 1.5834e-08 | 255.3704 | 255.3704 | 255.3704 | 255.3704 | 25.537 | 25.537 | 25.537 | 25.537 | 50900 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 9.1853e-10 | 9.1853e-10 | 47.1296 | 47.1296 | 47.1296 | 47.1296 | 4.713 | 4.713 | 4.713 | 4.713 | 1761800 | 32.6259 | 32.6259 | 32.6259 | 32.6259 | 3.1793e-08 | 3.1793e-08 | 1631.2963 | 1631.2963 | 1631.2963 | 1631.2963 | 163.1296 | 163.1296 | 163.1296 | 163.1296
MR-213 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Reading | 2-Way Meter - Water shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ WaterMtr per ¦ x on-demand Mtr read cmd | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | MR-212 |  |  | 0.066667 | 1 | WaterMtr | WaterMtr | 5 | 5 | 50 | 1 | 1.8519e-05 | 1.8519e-05 | 126200 | 2.337 | 2.337 | 2.337 | 2.337 | 3.2384e-06 | 3.2384e-06 | 116.8519 | 116.8519 | 116.8519 | 116.8519 | 11.6852 | 11.6852 | 11.6852 | 11.6852 | 383600 | 7.1037 | 7.1037 | 7.1037 | 7.1037 | 7.9125e-07 | 7.9125e-07 | 355.1852 | 355.1852 | 355.1852 | 355.1852 | 35.5185 | 35.5185 | 35.5185 | 35.5185 | 909500 | 16.8426 | 16.8426 | 16.8426 | 16.8426 | 2.3339e-05 | 2.3339e-05 | 842.1296 | 842.1296 | 842.1296 | 842.1296 | 84.213 | 84.213 | 84.213 | 84.213 | 279400 | 5.1741 | 5.1741 | 5.1741 | 5.1741 | 1.6041e-08 | 1.6041e-08 | 258.7037 | 258.7037 | 258.7037 | 258.7037 | 25.8704 | 25.8704 | 25.8704 | 25.8704 | 25600 | 0.47407 | 0.47407 | 0.47407 | 0.47407 | 4.6197e-10 | 4.6197e-10 | 23.7037 | 23.7037 | 23.7037 | 23.7037 | 2.3704 | 2.3704 | 2.3704 | 2.3704 | 1724300 | 31.9315 | 31.9315 | 31.9315 | 31.9315 | 3.1116e-08 | 3.1116e-08 | 1596.5741 | 1596.5741 | 1596.5741 | 1596.5741 | 159.6574 | 159.6574 | 159.6574 | 159.6574
MR-294 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Meter Reading | 2-Way Meter - Gas shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | MR-293 |  |  | 0.066667 | 1 | GasMtr | GasMtr | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 180200 | 0.083426 | 0.083426 | 0.083426 | 0.083426 | 2.3121e-07 | 2.3121e-07 | 8.3426 | 8.3426 | 8.3426 | 8.3426 | 0.41713 | 0.41713 | 0.41713 | 0.41713 | 544600 | 0.25213 | 0.25213 | 0.25213 | 0.25213 | 5.6167e-08 | 5.6167e-08 | 25.213 | 25.213 | 25.213 | 25.213 | 1.2606 | 1.2606 | 1.2606 | 1.2606 | 710300 | 0.32884 | 0.32884 | 0.32884 | 0.32884 | 9.1136e-07 | 9.1136e-07 | 32.8843 | 32.8843 | 32.8843 | 32.8843 | 1.6442 | 1.6442 | 1.6442 | 1.6442 | 275800 | 0.12769 | 0.12769 | 0.12769 | 0.12769 | 7.9172e-10 | 7.9172e-10 | 12.7685 | 12.7685 | 12.7685 | 12.7685 | 0.63843 | 0.63843 | 0.63843 | 0.63843 | 50900 | 0.023565 | 0.023565 | 0.023565 | 0.023565 | 4.5927e-11 | 4.5927e-11 | 2.3565 | 2.3565 | 2.3565 | 2.3565 | 0.11782 | 0.11782 | 0.11782 | 0.11782 | 1761800 | 0.81565 | 0.81565 | 0.81565 | 0.81565 | 1.5897e-09 | 1.5897e-09 | 81.5648 | 81.5648 | 81.5648 | 81.5648 | 4.0782 | 4.0782 | 4.0782 | 4.0782
MR-309 | c | 1Dw | 2-Way Meter - Water | DAPjm | Meter Reading | 2-Way Meter - Water shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 per 1000 per ¦ WaterMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | MR-308 |  |  | 0.066667 | 1 | WaterMtr | WaterMtr | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 126200 | 0.058426 | 0.058426 | 0.058426 | 0.058426 | 1.6192e-07 | 1.6192e-07 | 5.8426 | 5.8426 | 5.8426 | 5.8426 | 0.29213 | 0.29213 | 0.29213 | 0.29213 | 383600 | 0.17759 | 0.17759 | 0.17759 | 0.17759 | 3.9562e-08 | 3.9562e-08 | 17.7593 | 17.7593 | 17.7593 | 17.7593 | 0.88796 | 0.88796 | 0.88796 | 0.88796 | 909500 | 0.42106 | 0.42106 | 0.42106 | 0.42106 | 1.1669e-06 | 1.1669e-06 | 42.1065 | 42.1065 | 42.1065 | 42.1065 | 2.1053 | 2.1053 | 2.1053 | 2.1053 | 279400 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 8.0206e-10 | 8.0206e-10 | 12.9352 | 12.9352 | 12.9352 | 12.9352 | 0.64676 | 0.64676 | 0.64676 | 0.64676 | 25600 | 0.011852 | 0.011852 | 0.011852 | 0.011852 | 2.3099e-11 | 2.3099e-11 | 1.1852 | 1.1852 | 1.1852 | 1.1852 | 0.059259 | 0.059259 | 0.059259 | 0.059259 | 1724300 | 0.79829 | 0.79829 | 0.79829 | 0.79829 | 1.5558e-09 | 1.5558e-09 | 79.8287 | 79.8287 | 79.8287 | 79.8287 | 3.9914 | 3.9914 | 3.9914 | 3.9914
ORM-002 | c | 1D | 2-Way Meter - Electr | DAPjm | ORM | 2-Way Meter - Electr shall be able to send outage notifications to the DAPjm | otg_ntf_evnt_data | alarm | 24x7 | 1 per ¦ ElectrMtr per ¦ lost-power-event | > 98% | < 5 sec | 25 | event |  | X | X | up |  | x | ORM-001 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr-lost-power | 5 | 5 | 25 | 1 | 2.3148e-09 | 5.787e-06 | 206400 | 0.00047778 | 1.1944 | 0.00047778 | 1.1944 | 3.3103e-10 | 8.2758e-07 | 0.011944 | 29.8611 | 0.011944 | 29.8611 | 0.0023889 | 5.9722 | 0.0023889 | 5.9722 | 615700 | 0.0014252 | 3.5631 | 0.0014252 | 3.5631 | 7.9375e-11 | 1.9844e-07 | 0.035631 | 89.077 | 0.035631 | 89.077 | 0.0071262 | 17.8154 | 0.0071262 | 17.8154 | 882800 | 0.0020435 | 5.1088 | 0.0020435 | 5.1088 | 1.4159e-09 | 3.5396e-06 | 0.051088 | 127.7199 | 0.051088 | 127.7199 | 0.010218 | 25.544 | 0.010218 | 25.544 | 485900 | 0.0011248 | 2.8119 | 0.0011248 | 2.8119 | 1.7436e-12 | 4.3589e-09 | 0.028119 | 70.298 | 0.028119 | 70.298 | 0.0056238 | 14.0596 | 0.0056238 | 14.0596 | 107700 | 0.00024931 | 0.62326 | 0.00024931 | 0.62326 | 1.2147e-13 | 3.0368e-10 | 0.0062326 | 15.5816 | 0.0062326 | 15.5816 | 0.0012465 | 3.1163 | 0.0012465 | 3.1163 | 2298500 | 0.0053206 | 13.3015 | 0.0053206 | 13.3015 | 2.5924e-12 | 6.481e-09 | 0.13302 | 332.5376 | 0.13302 | 332.5376 | 0.026603 | 66.5075 | 0.026603 | 66.5075
ORM-013 | c | 1D | 2-Way Meter - Electr | DAPjm | ORM | 2-Way Meter - Electr shall be able to send power restoration notifications to the DAPjm | svc_rst_ntf_evnt_data | alert | 24x7 | 1 per ¦ ElectrMtr per ¦ power-returned-event | > 98% | < 5 sec | 25 | event |  | X | X | up |  | x | ORM-012 |  |  | 0.041667 | 1 | ElectrMtr | ElectrMtr-power-returned | 5 | 5 | 25 | 1 | 2.3148e-09 | 8.2672e-07 | 206400 | 0.00047778 | 0.17063 | 0.00047778 | 0.17063 | 3.3103e-10 | 1.1823e-07 | 0.011944 | 4.2659 | 0.011944 | 4.2659 | 0.0023889 | 0.85317 | 0.0023889 | 0.85317 | 615700 | 0.0014252 | 0.50901 | 0.0014252 | 0.50901 | 7.9375e-11 | 2.8348e-08 | 0.035631 | 12.7253 | 0.035631 | 12.7253 | 0.0071262 | 2.5451 | 0.0071262 | 2.5451 | 882800 | 0.0020435 | 0.72983 | 0.0020435 | 0.72983 | 1.4159e-09 | 5.0566e-07 | 0.051088 | 18.2457 | 0.051088 | 18.2457 | 0.010218 | 3.6491 | 0.010218 | 3.6491 | 485900 | 0.0011248 | 0.4017 | 0.0011248 | 0.4017 | 1.7436e-12 | 6.227e-10 | 0.028119 | 10.0426 | 0.028119 | 10.0426 | 0.0056238 | 2.0085 | 0.0056238 | 2.0085 | 107700 | 0.00024931 | 0.089038 | 0.00024931 | 0.089038 | 1.2147e-13 | 4.3382e-11 | 0.0062326 | 2.2259 | 0.0062326 | 2.2259 | 0.0012465 | 0.44519 | 0.0012465 | 0.44519 | 2298500 | 0.0053206 | 1.9002 | 0.0053206 | 1.9002 | 2.5924e-12 | 9.2585e-10 | 0.13302 | 47.5054 | 0.13302 | 47.5054 | 0.026603 | 9.5011 | 0.026603 | 9.5011
PHEV-020 | c | 5Ba | DAPjm | ESI - In Meter | PHEV | DAPjm shall be able to send charging price rates to ESI - In Meter | PHEV_price_rate_cmd | cmd | 7AM - 10PM | 1 per ¦ ESIInMtr-connected-PHEV per ¦ 2-4 per day | > 98% | < 10 sec | 255 | day |  | X | X | down |  | x | PHEV-001 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-connected-PHEV | 10 | 10 | 255 | 1 | 5.5556e-05 | 5.5556e-05 | 4128 | 0.22933 | 0.22933 | 0.22933 | 0.22933 | 1.6207e-06 | 1.6207e-06 | 58.48 | 58.48 | 58.48 | 58.48 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 12314 | 0.68411 | 0.68411 | 0.68411 | 0.68411 | 3.8862e-07 | 3.8862e-07 | 174.4483 | 174.4483 | 174.4483 | 174.4483 | 6.8411 | 6.8411 | 6.8411 | 6.8411 | 88280 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 3.466e-05 | 3.466e-05 | 1250.6333 | 1250.6333 | 1250.6333 | 1250.6333 | 49.0444 | 49.0444 | 49.0444 | 49.0444 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 5.8179 | 5.8179 | 5.8179 | 5.8179 | 2.8914e-08 | 2.8914e-08 | 1483.5617 | 1483.5617 | 1483.5617 | 1483.5617 | 58.1789 | 58.1789 | 58.1789 | 58.1789
PHEV-023 | c | 5Ba | DAPjm | ESI - In Meter | PHEV | DAPjm shall be able to process & send "negotiate Power Charging Rate messages (from PHEV) to LMS - Utility" communication failure to ESI - In Meter | PHEV_pwr_chrg_rate_comm_err | comm-err | 7AM - 10PM | 1 per 1000 per ¦ ESIInMtr-PHEV per ¦ day | > 98% | < 5 sec | 50 | day |  | X | X | down |  | x | PHEV-009 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-PHEV | 5 | 5 | 50 | 1 | 1.8519e-08 | 1.8519e-08 | 4128 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 1.0593e-10 | 1.0593e-10 | 0.0038222 | 0.0038222 | 0.0038222 | 0.0038222 | 0.00038222 | 0.00038222 | 0.00038222 | 0.00038222 | 12314 | 0.00022804 | 0.00022804 | 0.00022804 | 0.00022804 | 2.54e-11 | 2.54e-11 | 0.011402 | 0.011402 | 0.011402 | 0.011402 | 0.0011402 | 0.0011402 | 0.0011402 | 0.0011402 | 88280 | 0.0016348 | 0.0016348 | 0.0016348 | 0.0016348 | 2.2654e-09 | 2.2654e-09 | 0.081741 | 0.081741 | 0.081741 | 0.081741 | 0.0081741 | 0.0081741 | 0.0081741 | 0.0081741 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 0.0019393 | 0.0019393 | 0.0019393 | 0.0019393 | 1.8898e-12 | 1.8898e-12 | 0.096965 | 0.096965 | 0.096965 | 0.096965 | 0.0096965 | 0.0096965 | 0.0096965 | 0.0096965
PHEV-027 | c | 5Ba | DAPjm | ESI - In Meter | PHEV | DAPjm shall be able to forward negotiate Power Charging Rate messages (from LMS - Utility) to ESI - In Meter | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd | 7AM - 10PM | 2-4 per ¦ ESIInMtr-connected-PHEV per ¦ day | > 98% | < 10 sec | 100 | day |  | X | X | down |  | x | PHEV-003 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-connected-PHEV | 10 | 10 | 100 | 1 | 5.5556e-05 | 5.5556e-05 | 4128 | 0.22933 | 0.22933 | 0.22933 | 0.22933 | 6.3558e-07 | 6.3558e-07 | 22.9333 | 22.9333 | 22.9333 | 22.9333 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 12314 | 0.68411 | 0.68411 | 0.68411 | 0.68411 | 1.524e-07 | 1.524e-07 | 68.4111 | 68.4111 | 68.4111 | 68.4111 | 6.8411 | 6.8411 | 6.8411 | 6.8411 | 88280 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 1.3592e-05 | 1.3592e-05 | 490.4444 | 490.4444 | 490.4444 | 490.4444 | 49.0444 | 49.0444 | 49.0444 | 49.0444 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 5.8179 | 5.8179 | 5.8179 | 5.8179 | 1.1339e-08 | 1.1339e-08 | 581.7889 | 581.7889 | 581.7889 | 581.7889 | 58.1789 | 58.1789 | 58.1789 | 58.1789
PHEV-031 | c | 5Ba | DAPjm | ESI - In Meter | PHEV | DAPjm shall be able to process & send "PHEV VIN information request to MDMS (from PHEV)" communications failure to ESI - In Meter | PHEV_Vin_data_comm_err | comm-err | 7AM - 10PM | 1 per 1000 per ¦ ESIInMtr-connected-PHEV per ¦ day | > 99% | < 10 sec | 50 | day |  | X | X | down |  | x | PHEV-018 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-connected-PHEV | 10 | 10 | 50 | 1 | 1.8519e-08 | 1.8519e-08 | 4128 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 1.0593e-10 | 1.0593e-10 | 0.0038222 | 0.0038222 | 0.0038222 | 0.0038222 | 0.00076444 | 0.00076444 | 0.00076444 | 0.00076444 | 12314 | 0.00022804 | 0.00022804 | 0.00022804 | 0.00022804 | 2.54e-11 | 2.54e-11 | 0.011402 | 0.011402 | 0.011402 | 0.011402 | 0.0022804 | 0.0022804 | 0.0022804 | 0.0022804 | 88280 | 0.0016348 | 0.0016348 | 0.0016348 | 0.0016348 | 2.2654e-09 | 2.2654e-09 | 0.081741 | 0.081741 | 0.081741 | 0.081741 | 0.016348 | 0.016348 | 0.016348 | 0.016348 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 0.0019393 | 0.0019393 | 0.0019393 | 0.0019393 | 1.8898e-12 | 1.8898e-12 | 0.096965 | 0.096965 | 0.096965 | 0.096965 | 0.019393 | 0.019393 | 0.019393 | 0.019393
PHEV-045 | c | 5Ba | ESI - In Meter | DAPjm | PHEV | ESI - In Meter shall be able to forward "Send of Price Rate (from LM) to PHEV" communication failure to DAPjm | PHEV_price_rate_comm_err | comm-err | 7AM - 10PM | 1 per 1000 per ¦ ESIInMtr-PHEV per ¦ day | > 98% | < 10 sec | 50 | day |  | X | X | up |  | x | PHEV-046 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-PHEV | 10 | 10 | 50 | 1 | 1.8519e-08 | 1.8519e-08 | 4128 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 7.6444e-05 | 1.0593e-10 | 1.0593e-10 | 0.0038222 | 0.0038222 | 0.0038222 | 0.0038222 | 0.00076444 | 0.00076444 | 0.00076444 | 0.00076444 | 12314 | 0.00022804 | 0.00022804 | 0.00022804 | 0.00022804 | 2.54e-11 | 2.54e-11 | 0.011402 | 0.011402 | 0.011402 | 0.011402 | 0.0022804 | 0.0022804 | 0.0022804 | 0.0022804 | 88280 | 0.0016348 | 0.0016348 | 0.0016348 | 0.0016348 | 2.2654e-09 | 2.2654e-09 | 0.081741 | 0.081741 | 0.081741 | 0.081741 | 0.016348 | 0.016348 | 0.016348 | 0.016348 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 0.0019393 | 0.0019393 | 0.0019393 | 0.0019393 | 1.8898e-12 | 1.8898e-12 | 0.096965 | 0.096965 | 0.096965 | 0.096965 | 0.019393 | 0.019393 | 0.019393 | 0.019393
PHEV-050 | c | 5Ba | ESI - In Meter | DAPjm | PHEV | ESI - In Meter shall be able to forward negotiate Power Charging Rate messages (from PHEV) to DAPjm | PHEV_pwr_chrg_rate_negot-thrd | negot-thrd | 7AM - 10PM | 1 per ¦ ESIInMtr-connected-PHEV per ¦ 2-4 per day | > 98% | < 10 sec | 100 | day |  | X | X | up |  | x | PHEV-057 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-connected-PHEV | 10 | 10 | 100 | 1 | 5.5556e-05 | 5.5556e-05 | 4128 | 0.22933 | 0.22933 | 0.22933 | 0.22933 | 6.3558e-07 | 6.3558e-07 | 22.9333 | 22.9333 | 22.9333 | 22.9333 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 12314 | 0.68411 | 0.68411 | 0.68411 | 0.68411 | 1.524e-07 | 1.524e-07 | 68.4111 | 68.4111 | 68.4111 | 68.4111 | 6.8411 | 6.8411 | 6.8411 | 6.8411 | 88280 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 1.3592e-05 | 1.3592e-05 | 490.4444 | 490.4444 | 490.4444 | 490.4444 | 49.0444 | 49.0444 | 49.0444 | 49.0444 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 5.8179 | 5.8179 | 5.8179 | 5.8179 | 1.1339e-08 | 1.1339e-08 | 581.7889 | 581.7889 | 581.7889 | 581.7889 | 58.1789 | 58.1789 | 58.1789 | 58.1789
PHEV-052 | c | 5Ba | ESI - In Meter | DAPjm | PHEV | ESI - In Metershall be able to forward charging status of the PHEV to DAPjm | PHEV_pwr_chrg_status_resp-data | resp-data | 7AM - 10PM | 2-4 per ¦ ESIInMtr-PHEV per ¦ charging event per day | > 98% | < 10 sec | 100 | event-day |  | X | X | up |  | x | PHEV-060 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-PHEV | 10 | 10 | 100 | 1 | 5.5556e-05 | 5.5556e-05 | 4128 | 0.22933 | 0.22933 | 0.22933 | 0.22933 | 6.3558e-07 | 6.3558e-07 | 22.9333 | 22.9333 | 22.9333 | 22.9333 | 2.2933 | 2.2933 | 2.2933 | 2.2933 | 12314 | 0.68411 | 0.68411 | 0.68411 | 0.68411 | 1.524e-07 | 1.524e-07 | 68.4111 | 68.4111 | 68.4111 | 68.4111 | 6.8411 | 6.8411 | 6.8411 | 6.8411 | 88280 | 4.9044 | 4.9044 | 4.9044 | 4.9044 | 1.3592e-05 | 1.3592e-05 | 490.4444 | 490.4444 | 490.4444 | 490.4444 | 49.0444 | 49.0444 | 49.0444 | 49.0444 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 5.8179 | 5.8179 | 5.8179 | 5.8179 | 1.1339e-08 | 1.1339e-08 | 581.7889 | 581.7889 | 581.7889 | 581.7889 | 58.1789 | 58.1789 | 58.1789 | 58.1789
PHEV-053 | c | 5Ba | ESI - In Meter | DAPjm | PHEV | ESI - In Meter shall be able to forward PHEV VIN information request to DAPjm | PHEV_Vin_data_cmd | cmd | 7AM - 10PM | 1 per ¦ ESIInMtr-connected-PHEV per ¦ day | > 98% | < 10 sec | 50 | day |  | X | X | up |  | x | PHEV-064 |  |  | 0.066667 | 1 | PHEV | ESIInMtr-connected-PHEV | 10 | 10 | 50 | 1 | 1.8519e-05 | 1.8519e-05 | 4128 | 0.076444 | 0.076444 | 0.076444 | 0.076444 | 1.0593e-07 | 1.0593e-07 | 3.8222 | 3.8222 | 3.8222 | 3.8222 | 0.76444 | 0.76444 | 0.76444 | 0.76444 | 12314 | 0.22804 | 0.22804 | 0.22804 | 0.22804 | 2.54e-08 | 2.54e-08 | 11.4019 | 11.4019 | 11.4019 | 11.4019 | 2.2804 | 2.2804 | 2.2804 | 2.2804 | 88280 | 1.6348 | 1.6348 | 1.6348 | 1.6348 | 2.2654e-06 | 2.2654e-06 | 81.7407 | 81.7407 | 81.7407 | 81.7407 | 16.3481 | 16.3481 | 16.3481 | 16.3481 | [12 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104722 | 1.9393 | 1.9393 | 1.9393 | 1.9393 | 1.8898e-09 | 1.8898e-09 | 96.9648 | 96.9648 | 96.9648 | 96.9648 | 19.393 | 19.393 | 19.393 | 19.393
PNA-197 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device join request cmd errors to the DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ElectrMtr-with-HANdevice per ¦ join request per day | > 98% | < 5 sec | 25 | request-day |  | X | X | up |  | x | PNA-196 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-with-HANdevice-join | 5 | 5 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 10320 | 5.9722e-06 | 3.5833e-05 | 5.9722e-06 | 3.5833e-05 | 4.1379e-12 | 2.4827e-11 | 0.00014931 | 0.00089583 | 0.00014931 | 0.00089583 | 2.9861e-05 | 0.00017917 | 2.9861e-05 | 0.00017917 | 30785 | 1.7815e-05 | 0.00010689 | 1.7815e-05 | 0.00010689 | 9.9219e-13 | 5.9531e-12 | 0.00044538 | 0.0026723 | 0.00044538 | 0.0026723 | 8.9077e-05 | 0.00053446 | 8.9077e-05 | 0.00053446 | 44140 | 2.5544e-05 | 0.00017881 | 2.5544e-05 | 0.00017881 | 1.7698e-11 | 1.2389e-10 | 0.0006386 | 0.0044702 | 0.0006386 | 0.0044702 | 0.00012772 | 0.00089404 | 0.00012772 | 0.00089404 | 24295 | 1.406e-05 | 4.2179e-05 | 1.406e-05 | 4.2179e-05 | 2.1795e-14 | 6.5384e-14 | 0.00035149 | 0.0010545 | 0.00035149 | 0.0010545 | 7.0298e-05 | 0.00021089 | 7.0298e-05 | 0.00021089 | 5385 | 3.1163e-06 | 9.349e-06 | 3.1163e-06 | 9.349e-06 | 1.5184e-15 | 4.5552e-15 | 7.7908e-05 | 0.00023372 | 7.7908e-05 | 0.00023372 | 1.5582e-05 | 4.6745e-05 | 1.5582e-05 | 4.6745e-05 | 114925 | 6.6508e-05 | 0.00037306 | 6.6508e-05 | 0.00037306 | 3.2405e-14 | 1.8177e-13 | 0.0016627 | 0.0093265 | 0.0016627 | 0.0093265 | 0.00033254 | 0.0018653 | 0.00033254 | 0.0018653
PNA-198 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-196 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 9010 | 5.2141e-06 | 3.1285e-05 | 5.2141e-06 | 3.1285e-05 | 3.6126e-12 | 2.1676e-11 | 0.00013035 | 0.00078212 | 0.00013035 | 0.00078212 | 0.00015642 | 0.00093854 | 0.00015642 | 0.00093854 | 27230 | 1.5758e-05 | 9.4549e-05 | 1.5758e-05 | 9.4549e-05 | 8.7761e-13 | 5.2657e-12 | 0.00039395 | 0.0023637 | 0.00039395 | 0.0023637 | 0.00047274 | 0.0028365 | 0.00047274 | 0.0028365 | 35515 | 2.0553e-05 | 0.00014387 | 2.0553e-05 | 0.00014387 | 1.424e-11 | 9.968e-11 | 0.00051382 | 0.0035967 | 0.00051382 | 0.0035967 | 0.00061658 | 0.0043161 | 0.00061658 | 0.0043161 | 13790 | 7.9803e-06 | 2.3941e-05 | 7.9803e-06 | 2.3941e-05 | 1.2371e-14 | 3.7112e-14 | 0.00019951 | 0.00059852 | 0.00019951 | 0.00059852 | 0.00023941 | 0.00071823 | 0.00023941 | 0.00071823 | 2545 | 1.4728e-06 | 4.4184e-06 | 1.4728e-06 | 4.4184e-06 | 7.176e-16 | 2.1528e-15 | 3.682e-05 | 0.00011046 | 3.682e-05 | 0.00011046 | 4.4184e-05 | 0.00013255 | 4.4184e-05 | 0.00013255 | 88090 | 5.0978e-05 | 0.00029806 | 5.0978e-05 | 0.00029806 | 2.4838e-14 | 1.4523e-13 | 0.0012745 | 0.0074515 | 0.0012745 | 0.0074515 | 0.0015293 | 0.0089418 | 0.0015293 | 0.0089418
PNA-200 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ESIInMtr-Mtr-with-HANdevice per ¦ join request per day | > 98% | < 5 sec | 25 | request-day |  | X | X | up |  | x | PNA-196 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-Mtr-with-HANdevice-join | 5 | 5 | 25 | 1 | 6.9444e-08 | 6.9444e-08 | 10320 | 3.5833e-05 | 0.000215 | 3.5833e-05 | 0.000215 | 2.4827e-11 | 1.4896e-10 | 0.00089583 | 0.005375 | 0.00089583 | 0.005375 | 0.00017917 | 0.001075 | 0.00017917 | 0.001075 | 30785 | 0.00010689 | 0.00064135 | 0.00010689 | 0.00064135 | 5.9531e-12 | 3.5719e-11 | 0.0026723 | 0.016034 | 0.0026723 | 0.016034 | 0.00053446 | 0.0032068 | 0.00053446 | 0.0032068 | 44140 | 0.00015326 | 0.0010728 | 0.00015326 | 0.0010728 | 1.0619e-10 | 7.4333e-10 | 0.0038316 | 0.026821 | 0.0038316 | 0.026821 | 0.00076632 | 0.0053642 | 0.00076632 | 0.0053642 | 24295 | 8.4358e-05 | 0.00025307 | 8.4358e-05 | 0.00025307 | 1.3077e-13 | 3.923e-13 | 0.0021089 | 0.0063268 | 0.0021089 | 0.0063268 | 0.00042179 | 0.0012654 | 0.00042179 | 0.0012654 | 5385 | 1.8698e-05 | 5.6094e-05 | 1.8698e-05 | 5.6094e-05 | 9.1103e-15 | 2.7331e-14 | 0.00046745 | 0.0014023 | 0.00046745 | 0.0014023 | 9.349e-05 | 0.00028047 | 9.349e-05 | 0.00028047 | 114925 | 0 | 0.0022384 | 0 | 0.0022384 | 0 | 1.0906e-12 | 0 | 0.055959 | 0 | 0.055959 | 0 | 0.011192 | 0 | 0.011192
PNA-203 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ WaterMtr-with-HANdevice per ¦ join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-196 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-with-HANdevice-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 6310 | 3.6516e-06 | 2.191e-05 | 3.6516e-06 | 2.191e-05 | 2.53e-12 | 1.518e-11 | 9.1291e-05 | 0.00054774 | 9.1291e-05 | 0.00054774 | 0.00010955 | 0.00065729 | 0.00010955 | 0.00065729 | 19180 | 1.11e-05 | 6.6597e-05 | 1.11e-05 | 6.6597e-05 | 6.1816e-13 | 3.709e-12 | 0.00027749 | 0.0016649 | 0.00027749 | 0.0016649 | 0.00033299 | 0.0019979 | 0.00033299 | 0.0019979 | 45475 | 2.6317e-05 | 0.00018422 | 2.6317e-05 | 0.00018422 | 1.8234e-11 | 1.2763e-10 | 0.00065791 | 0.0046054 | 0.00065791 | 0.0046054 | 0.0007895 | 0.0055265 | 0.0007895 | 0.0055265 | 13970 | 8.0845e-06 | 2.4253e-05 | 8.0845e-06 | 2.4253e-05 | 1.2532e-14 | 3.7597e-14 | 0.00020211 | 0.00060634 | 0.00020211 | 0.00060634 | 0.00024253 | 0.0007276 | 0.00024253 | 0.0007276 | 1280 | 7.4074e-07 | 2.2222e-06 | 7.4074e-07 | 2.2222e-06 | 3.6092e-16 | 1.0827e-15 | 1.8519e-05 | 5.5556e-05 | 1.8519e-05 | 5.5556e-05 | 2.2222e-05 | 6.6667e-05 | 2.2222e-05 | 6.6667e-05 | 86215 | 4.9893e-05 | 0.0002992 | 4.9893e-05 | 0.0002992 | 2.431e-14 | 1.4578e-13 | 0.0012473 | 0.00748 | 0.0012473 | 0.00748 | 0.0014968 | 0.008976 | 0.0014968 | 0.008976
PNA-273 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device un-join request cmd errors to the DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ElectrMtr-with-HANdevice per ¦ un-join request per day | > 98% | < 5 sec | 25 | request-day |  | X | X | up |  | x | PNA-272 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-with-HANdevice-un-join | 5 | 5 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 10320 | 0.00011944 | 0.00011944 | 0.00011944 | 0.00011944 | 8.2758e-11 | 8.2758e-11 | 0.0029861 | 0.0029861 | 0.0029861 | 0.0029861 | 0.00059722 | 0.00059722 | 0.00059722 | 0.00059722 | 30785 | 0.00035631 | 0.00035631 | 0.00035631 | 0.00035631 | 1.9844e-11 | 1.9844e-11 | 0.0089077 | 0.0089077 | 0.0089077 | 0.0089077 | 0.0017815 | 0.0017815 | 0.0017815 | 0.0017815 | 44140 | 0.00051088 | 0.00051088 | 0.00051088 | 0.00051088 | 3.5396e-10 | 3.5396e-10 | 0.012772 | 0.012772 | 0.012772 | 0.012772 | 0.0025544 | 0.0025544 | 0.0025544 | 0.0025544 | 24295 | 0.00028119 | 0.00028119 | 0.00028119 | 0.00028119 | 4.3589e-13 | 4.3589e-13 | 0.0070298 | 0.0070298 | 0.0070298 | 0.0070298 | 0.001406 | 0.001406 | 0.001406 | 0.001406 | 5385 | 6.2326e-05 | 6.2326e-05 | 6.2326e-05 | 6.2326e-05 | 3.0368e-14 | 3.0368e-14 | 0.0015582 | 0.0015582 | 0.0015582 | 0.0015582 | 0.00031163 | 0.00031163 | 0.00031163 | 0.00031163 | 114925 | 0.0013302 | 0.0013302 | 0.0013302 | 0.0013302 | 6.481e-13 | 6.481e-13 | 0.033254 | 0.033254 | 0.033254 | 0.033254 | 0.0066508 | 0.0066508 | 0.0066508 | 0.0066508
PNA-274 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ un-join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-272 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-un-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 9010 | 0.00010428 | 0.00010428 | 0.00010428 | 0.00010428 | 7.2252e-11 | 7.2252e-11 | 0.0026071 | 0.0026071 | 0.0026071 | 0.0026071 | 0.0031285 | 0.0031285 | 0.0031285 | 0.0031285 | 27230 | 0.00031516 | 0.00031516 | 0.00031516 | 0.00031516 | 1.7552e-11 | 1.7552e-11 | 0.0078791 | 0.0078791 | 0.0078791 | 0.0078791 | 0.0094549 | 0.0094549 | 0.0094549 | 0.0094549 | 35515 | 0.00041105 | 0.00041105 | 0.00041105 | 0.00041105 | 2.848e-10 | 2.848e-10 | 0.010276 | 0.010276 | 0.010276 | 0.010276 | 0.012332 | 0.012332 | 0.012332 | 0.012332 | 13790 | 0.00015961 | 0.00015961 | 0.00015961 | 0.00015961 | 2.4741e-13 | 2.4741e-13 | 0.0039902 | 0.0039902 | 0.0039902 | 0.0039902 | 0.0047882 | 0.0047882 | 0.0047882 | 0.0047882 | 2545 | 2.9456e-05 | 2.9456e-05 | 2.9456e-05 | 2.9456e-05 | 1.4352e-14 | 1.4352e-14 | 0.0007364 | 0.0007364 | 0.0007364 | 0.0007364 | 0.00088368 | 0.00088368 | 0.00088368 | 0.00088368 | 88090 | 0.0010196 | 0.0010196 | 0.0010196 | 0.0010196 | 4.9677e-13 | 4.9677e-13 | 0.025489 | 0.025489 | 0.025489 | 0.025489 | 0.030587 | 0.030587 | 0.030587 | 0.030587
PNA-276 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ESIInMtr-Mtr-with-HANdevice per ¦ un-join request per day | > 98% | < 5 sec | 25 | request-day |  | X | X | up |  | x | PNA-272 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-Mtr-with-HANdevice-un-join | 5 | 5 | 25 | 1 | 6.9444e-08 | 6.9444e-08 | 10320 | 0.00071667 | 0.00071667 | 0.00071667 | 0.00071667 | 4.9655e-10 | 4.9655e-10 | 0.017917 | 0.017917 | 0.017917 | 0.017917 | 0.0035833 | 0.0035833 | 0.0035833 | 0.0035833 | 30785 | 0.0021378 | 0.0021378 | 0.0021378 | 0.0021378 | 1.1906e-10 | 1.1906e-10 | 0.053446 | 0.053446 | 0.053446 | 0.053446 | 0.010689 | 0.010689 | 0.010689 | 0.010689 | 44140 | 0.0030653 | 0.0030653 | 0.0030653 | 0.0030653 | 2.1238e-09 | 2.1238e-09 | 0.076632 | 0.076632 | 0.076632 | 0.076632 | 0.015326 | 0.015326 | 0.015326 | 0.015326 | 24295 | 0.0016872 | 0.0016872 | 0.0016872 | 0.0016872 | 2.6153e-12 | 2.6153e-12 | 0.042179 | 0.042179 | 0.042179 | 0.042179 | 0.0084358 | 0.0084358 | 0.0084358 | 0.0084358 | 5385 | 0.00037396 | 0.00037396 | 0.00037396 | 0.00037396 | 1.8221e-13 | 1.8221e-13 | 0.009349 | 0.009349 | 0.009349 | 0.009349 | 0.0018698 | 0.0018698 | 0.0018698 | 0.0018698 | 114925 | 0.0079809 | 0.0079809 | 0.0079809 | 0.0079809 | 3.8886e-12 | 3.8886e-12 | 0.19952 | 0.19952 | 0.19952 | 0.19952 | 0.039905 | 0.039905 | 0.039905 | 0.039905
PNA-279 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ WaterMtr-with-HANdevice per ¦ un-join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-272 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-with-HANdevice-un-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 6310 | 3.6516e-06 | 2.191e-05 | 3.6516e-06 | 2.191e-05 | 2.53e-12 | 1.518e-11 | 9.1291e-05 | 0.00054774 | 9.1291e-05 | 0.00054774 | 0.00010955 | 0.00065729 | 0.00010955 | 0.00065729 | 19180 | 1.11e-05 | 6.6597e-05 | 1.11e-05 | 6.6597e-05 | 6.1816e-13 | 3.709e-12 | 0.00027749 | 0.0016649 | 0.00027749 | 0.0016649 | 0.00033299 | 0.0019979 | 0.00033299 | 0.0019979 | 45475 | 2.6317e-05 | 0.00018422 | 2.6317e-05 | 0.00018422 | 1.8234e-11 | 1.2763e-10 | 0.00065791 | 0.0046054 | 0.00065791 | 0.0046054 | 0.0007895 | 0.0055265 | 0.0007895 | 0.0055265 | 13970 | 8.0845e-06 | 2.4253e-05 | 8.0845e-06 | 2.4253e-05 | 1.2532e-14 | 3.7597e-14 | 0.00020211 | 0.00060634 | 0.00020211 | 0.00060634 | 0.00024253 | 0.0007276 | 0.00024253 | 0.0007276 | 1280 | 7.4074e-07 | 2.2222e-06 | 7.4074e-07 | 2.2222e-06 | 3.6092e-16 | 1.0827e-15 | 1.8519e-05 | 5.5556e-05 | 1.8519e-05 | 5.5556e-05 | 2.2222e-05 | 6.6667e-05 | 2.2222e-05 | 6.6667e-05 | 86215 | 4.9893e-05 | 0.0002992 | 4.9893e-05 | 0.0002992 | 2.431e-14 | 1.4578e-13 | 0.0012473 | 0.00748 | 0.0012473 | 0.00748 | 0.0014968 | 0.008976 | 0.0014968 | 0.008976
PNA-318 | c | 1D | DAPjm | 2-Way Meter - Electr | Premise Network Admin | DAPjm shall be able to send HAN device join request to 2-Way Meter - Electr | han_dev_join_cmd | cmd | 24x7 | x per ¦ ElectrMtr per ¦ REPi join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | down |  | x | PNA-309 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-REPi-join | 5 | 5 | 25 | 1 | 3.171e-08 | 3.171e-08 | 10320 | 1.6362e-05 | 9.8174e-05 | 1.6362e-05 | 9.8174e-05 | 1.1337e-11 | 6.802e-11 | 0.00040906 | 0.0024543 | 0.00040906 | 0.0024543 | 8.1811e-05 | 0.00049087 | 8.1811e-05 | 0.00049087 | 30785 | 4.8809e-05 | 0.00029286 | 4.8809e-05 | 0.00029286 | 2.7183e-12 | 1.631e-11 | 0.0012202 | 0.0073214 | 0.0012202 | 0.0073214 | 0.00024405 | 0.0014643 | 0.00024405 | 0.0014643 | 44140 | 6.9984e-05 | 0.00048988 | 6.9984e-05 | 0.00048988 | 4.8488e-11 | 3.3942e-10 | 0.0017496 | 0.012247 | 0.0017496 | 0.012247 | 0.00034992 | 0.0024494 | 0.00034992 | 0.0024494 | 24295 | 3.8519e-05 | 0.00011556 | 3.8519e-05 | 0.00011556 | 5.9711e-14 | 1.7913e-13 | 0.00096299 | 0.002889 | 0.00096299 | 0.002889 | 0.0001926 | 0.00057779 | 0.0001926 | 0.00057779 | 5385 | 8.5379e-06 | 2.5614e-05 | 8.5379e-06 | 2.5614e-05 | 4.16e-15 | 1.248e-14 | 0.00021345 | 0.00064034 | 0.00021345 | 0.00064034 | 4.2689e-05 | 0.00012807 | 4.2689e-05 | 0.00012807 | 114925 | 0.00018221 | 0.0010221 | 0.00018221 | 0.0010221 | 8.878e-14 | 4.98e-13 | 0.0045553 | 0.025552 | 0.0045553 | 0.025552 | 0.00091106 | 0.0051104 | 0.00091106 | 0.0051104
PNA-319 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Premise Network Admin | DAPjm shall be able to process & forward HAN device join request to 2-Way Meter - Gas | han_dev_join_cmd | cmd | 24x7 | x per ¦ GasMtr per ¦ REPi-Mtr per day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | PNA-309 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-REPi-Mtr | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 9010 | 1.4285e-05 | 8.5712e-05 | 1.4285e-05 | 8.5712e-05 | 9.8976e-12 | 5.9386e-11 | 0.00035713 | 0.0021428 | 0.00035713 | 0.0021428 | 0.00042856 | 0.0025713 | 0.00042856 | 0.0025713 | 27230 | 4.3173e-05 | 0.00025904 | 4.3173e-05 | 0.00025904 | 2.4044e-12 | 1.4426e-11 | 0.0010793 | 0.0064759 | 0.0010793 | 0.0064759 | 0.0012952 | 0.0077711 | 0.0012952 | 0.0077711 | 35515 | 5.6309e-05 | 0.00039416 | 5.6309e-05 | 0.00039416 | 3.9014e-11 | 2.731e-10 | 0.0014077 | 0.009854 | 0.0014077 | 0.009854 | 0.0016893 | 0.011825 | 0.0016893 | 0.011825 | 13790 | 2.1864e-05 | 6.5592e-05 | 2.1864e-05 | 6.5592e-05 | 3.3892e-14 | 1.0168e-13 | 0.0005466 | 0.0016398 | 0.0005466 | 0.0016398 | 0.00065592 | 0.0019678 | 0.00065592 | 0.0019678 | 2545 | 4.0351e-06 | 1.2105e-05 | 4.0351e-06 | 1.2105e-05 | 1.966e-15 | 5.8981e-15 | 0.00010088 | 0.00030263 | 0.00010088 | 0.00030263 | 0.00012105 | 0.00036316 | 0.00012105 | 0.00036316 | 88090 | 0.00013967 | 0.00081661 | 0.00013967 | 0.00081661 | 6.805e-14 | 3.9788e-13 | 0.0034916 | 0.020415 | 0.0034916 | 0.020415 | 0.00419 | 0.024498 | 0.00419 | 0.024498
PNA-320 | c | 5Ba | DAPjm | ESI - In Meter | Premise Network Admin | DAPjm shall be able to process & forward HAN device join request to ESI - In Meter | han_dev_join_cmd | cmd | 24x7 | x per ¦ ESIInMtr-with-HANdevice per ¦ REPi join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | down |  | x | PNA-309 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-with-HANdevice-REPi-join | 5 | 5 | 25 | 1 | 1.9026e-07 | 1.9026e-07 | 10320 | 9.8174e-05 | 0.00058904 | 9.8174e-05 | 0.00058904 | 6.802e-11 | 4.0812e-10 | 0.0024543 | 0.014726 | 0.0024543 | 0.014726 | 0.00049087 | 0.0029452 | 0.00049087 | 0.0029452 | 30785 | 0.00029286 | 0.0017571 | 0.00029286 | 0.0017571 | 1.631e-11 | 9.7859e-11 | 0.0073214 | 0.043928 | 0.0073214 | 0.043928 | 0.0014643 | 0.0087857 | 0.0014643 | 0.0087857 | 44140 | 0.0004199 | 0.0029393 | 0.0004199 | 0.0029393 | 2.9093e-10 | 2.0365e-09 | 0.010498 | 0.073483 | 0.010498 | 0.073483 | 0.0020995 | 0.014697 | 0.0020995 | 0.014697 | 24295 | 0.00023112 | 0.00069335 | 0.00023112 | 0.00069335 | 3.5827e-13 | 1.0748e-12 | 0.0057779 | 0.017334 | 0.0057779 | 0.017334 | 0.0011556 | 0.0034668 | 0.0011556 | 0.0034668 | 5385 | 5.1227e-05 | 0.00015368 | 5.1227e-05 | 0.00015368 | 2.496e-14 | 7.4879e-14 | 0.0012807 | 0.003842 | 0.0012807 | 0.003842 | 0.00025614 | 0.00076841 | 0.00025614 | 0.00076841 | 114925 | 0.0010933 | 0.0061325 | 0.0010933 | 0.0061325 | 5.3268e-13 | 2.988e-12 | 0.027332 | 0.15331 | 0.027332 | 0.15331 | 0.0054664 | 0.030663 | 0.0054664 | 0.030663
PNA-324 | c | 1Dw | DAPjm | 2-Way Meter - Water | Premise Network Admin | DAPjm shall be able to process & forward HAN device join request to 2-Way Meter - Water | han_dev_join_cmd | cmd | 24x7 | x per ¦ WaterMtr per ¦ REPi join request per year | > 98% | < 30 sec | 25 | request-year |  | X | X | down |  | x | PNA-309 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-REPi-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 6310 | 1.0004e-05 | 6.0027e-05 | 1.0004e-05 | 6.0027e-05 | 6.9316e-12 | 4.159e-11 | 0.00025011 | 0.0015007 | 0.00025011 | 0.0015007 | 0.00030013 | 0.0018008 | 0.00030013 | 0.0018008 | 19180 | 3.041e-05 | 0.00018246 | 3.041e-05 | 0.00018246 | 1.6936e-12 | 1.0162e-11 | 0.00076024 | 0.0045615 | 0.00076024 | 0.0045615 | 0.00091229 | 0.0054737 | 0.00091229 | 0.0054737 | 45475 | 7.21e-05 | 0.0005047 | 7.21e-05 | 0.0005047 | 4.9955e-11 | 3.4968e-10 | 0.0018025 | 0.012618 | 0.0018025 | 0.012618 | 0.002163 | 0.015141 | 0.002163 | 0.015141 | 13970 | 2.2149e-05 | 6.6448e-05 | 2.2149e-05 | 6.6448e-05 | 3.4335e-14 | 1.03e-13 | 0.00055373 | 0.0016612 | 0.00055373 | 0.0016612 | 0.00066448 | 0.0019934 | 0.00066448 | 0.0019934 | 1280 | 2.0294e-06 | 6.0883e-06 | 2.0294e-06 | 6.0883e-06 | 9.8881e-16 | 2.9664e-15 | 5.0736e-05 | 0.00015221 | 5.0736e-05 | 0.00015221 | 6.0883e-05 | 0.00018265 | 6.0883e-05 | 0.00018265 | 86215 | 0.00013669 | 0.00081972 | 0.00013669 | 0.00081972 | 6.6602e-14 | 3.994e-13 | 0.0034173 | 0.020493 | 0.0034173 | 0.020493 | 0.0041008 | 0.024592 | 0.0041008 | 0.024592
PNA-352 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device join request acknowlegement to the DAPjm | han_dev_join_ack | ack | 24x7 | x per ¦ ElectrMtr per ¦ REPi join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | up |  | x | PNA-351 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-REPi-join | 5 | 5 | 25 | 1 | 3.171e-08 | 3.171e-08 | 10320 | 1.6362e-05 | 9.8174e-05 | 1.6362e-05 | 9.8174e-05 | 1.1337e-11 | 6.802e-11 | 0.00040906 | 0.0024543 | 0.00040906 | 0.0024543 | 8.1811e-05 | 0.00049087 | 8.1811e-05 | 0.00049087 | 30785 | 4.8809e-05 | 0.00029286 | 4.8809e-05 | 0.00029286 | 2.7183e-12 | 1.631e-11 | 0.0012202 | 0.0073214 | 0.0012202 | 0.0073214 | 0.00024405 | 0.0014643 | 0.00024405 | 0.0014643 | 44140 | 6.9984e-05 | 0.00048988 | 6.9984e-05 | 0.00048988 | 4.8488e-11 | 3.3942e-10 | 0.0017496 | 0.012247 | 0.0017496 | 0.012247 | 0.00034992 | 0.0024494 | 0.00034992 | 0.0024494 | 24295 | 3.8519e-05 | 0.00011556 | 3.8519e-05 | 0.00011556 | 5.9711e-14 | 1.7913e-13 | 0.00096299 | 0.002889 | 0.00096299 | 0.002889 | 0.0001926 | 0.00057779 | 0.0001926 | 0.00057779 | 5385 | 8.5379e-06 | 2.5614e-05 | 8.5379e-06 | 2.5614e-05 | 4.16e-15 | 1.248e-14 | 0.00021345 | 0.00064034 | 0.00021345 | 0.00064034 | 4.2689e-05 | 0.00012807 | 4.2689e-05 | 0.00012807 | 114925 | 0.00018221 | 0.0010221 | 0.00018221 | 0.0010221 | 8.878e-14 | 4.98e-13 | 0.0045553 | 0.025552 | 0.0045553 | 0.025552 | 0.00091106 | 0.0051104 | 0.00091106 | 0.0051104
PNA-353 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device join request acknowlegement to DAPjm | han_dev_join_ack | ack | 24x7 | x per ¦ GasMtr per ¦ REPi-Mtr-join-request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-351 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-repI-Mtr-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 9010 | 1.4285e-05 | 8.5712e-05 | 1.4285e-05 | 8.5712e-05 | 9.8976e-12 | 5.9386e-11 | 0.00035713 | 0.0021428 | 0.00035713 | 0.0021428 | 0.00042856 | 0.0025713 | 0.00042856 | 0.0025713 | 27230 | 4.3173e-05 | 0.00025904 | 4.3173e-05 | 0.00025904 | 2.4044e-12 | 1.4426e-11 | 0.0010793 | 0.0064759 | 0.0010793 | 0.0064759 | 0.0012952 | 0.0077711 | 0.0012952 | 0.0077711 | 35515 | 5.6309e-05 | 0.00039416 | 5.6309e-05 | 0.00039416 | 3.9014e-11 | 2.731e-10 | 0.0014077 | 0.009854 | 0.0014077 | 0.009854 | 0.0016893 | 0.011825 | 0.0016893 | 0.011825 | 13790 | 2.1864e-05 | 6.5592e-05 | 2.1864e-05 | 6.5592e-05 | 3.3892e-14 | 1.0168e-13 | 0.0005466 | 0.0016398 | 0.0005466 | 0.0016398 | 0.00065592 | 0.0019678 | 0.00065592 | 0.0019678 | 2545 | 4.0351e-06 | 1.2105e-05 | 4.0351e-06 | 1.2105e-05 | 1.966e-15 | 5.8981e-15 | 0.00010088 | 0.00030263 | 0.00010088 | 0.00030263 | 0.00012105 | 0.00036316 | 0.00012105 | 0.00036316 | 88090 | 0.00013967 | 0.00081661 | 0.00013967 | 0.00081661 | 6.805e-14 | 3.9788e-13 | 0.0034916 | 0.020415 | 0.0034916 | 0.020415 | 0.00419 | 0.024498 | 0.00419 | 0.024498
PNA-355 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device join request acknowledgements to DAPjm | han_dev_join_ack | ack | 24x7 | x per ¦ ESIInMtr-with-HANdevice per ¦ REPi join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | up |  | x | PNA-351 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-with-HANdevice-REPi-join | 5 | 5 | 25 | 1 | 1.9026e-07 | 1.9026e-07 | 10320 | 9.8174e-05 | 0.00058904 | 9.8174e-05 | 0.00058904 | 6.802e-11 | 4.0812e-10 | 0.0024543 | 0.014726 | 0.0024543 | 0.014726 | 0.00049087 | 0.0029452 | 0.00049087 | 0.0029452 | 30785 | 0.00029286 | 0.0017571 | 0.00029286 | 0.0017571 | 1.631e-11 | 9.7859e-11 | 0.0073214 | 0.043928 | 0.0073214 | 0.043928 | 0.0014643 | 0.0087857 | 0.0014643 | 0.0087857 | 44140 | 0.0004199 | 0.0029393 | 0.0004199 | 0.0029393 | 2.9093e-10 | 2.0365e-09 | 0.010498 | 0.073483 | 0.010498 | 0.073483 | 0.0020995 | 0.014697 | 0.0020995 | 0.014697 | 24295 | 0.00023112 | 0.00069335 | 0.00023112 | 0.00069335 | 3.5827e-13 | 1.0748e-12 | 0.0057779 | 0.017334 | 0.0057779 | 0.017334 | 0.0011556 | 0.0034668 | 0.0011556 | 0.0034668 | 5385 | 5.1227e-05 | 0.00015368 | 5.1227e-05 | 0.00015368 | 2.496e-14 | 7.4879e-14 | 0.0012807 | 0.003842 | 0.0012807 | 0.003842 | 0.00025614 | 0.00076841 | 0.00025614 | 0.00076841 | 114925 | 0.0010933 | 0.0061325 | 0.0010933 | 0.0061325 | 5.3268e-13 | 2.988e-12 | 0.027332 | 0.15331 | 0.027332 | 0.15331 | 0.0054664 | 0.030663 | 0.0054664 | 0.030663
PNA-358 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device join request acknowlegement to DAPjm | han_dev_join_ack | ack | 24x7 | x per ¦ WaterMtr per ¦ REPi join request per year | > 98% | < 30 sec | 25 | request-year |  | X | X | up |  | x | PNA-351 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-REPi-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 6310 | 1.0004e-05 | 6.0027e-05 | 1.0004e-05 | 6.0027e-05 | 6.9316e-12 | 4.159e-11 | 0.00025011 | 0.0015007 | 0.00025011 | 0.0015007 | 0.00030013 | 0.0018008 | 0.00030013 | 0.0018008 | 19180 | 3.041e-05 | 0.00018246 | 3.041e-05 | 0.00018246 | 1.6936e-12 | 1.0162e-11 | 0.00076024 | 0.0045615 | 0.00076024 | 0.0045615 | 0.00091229 | 0.0054737 | 0.00091229 | 0.0054737 | 45475 | 7.21e-05 | 0.0005047 | 7.21e-05 | 0.0005047 | 4.9955e-11 | 3.4968e-10 | 0.0018025 | 0.012618 | 0.0018025 | 0.012618 | 0.002163 | 0.015141 | 0.002163 | 0.015141 | 13970 | 2.2149e-05 | 6.6448e-05 | 2.2149e-05 | 6.6448e-05 | 3.4335e-14 | 1.03e-13 | 0.00055373 | 0.0016612 | 0.00055373 | 0.0016612 | 0.00066448 | 0.0019934 | 0.00066448 | 0.0019934 | 1280 | 2.0294e-06 | 6.0883e-06 | 2.0294e-06 | 6.0883e-06 | 9.8881e-16 | 2.9664e-15 | 5.0736e-05 | 0.00015221 | 5.0736e-05 | 0.00015221 | 6.0883e-05 | 0.00018265 | 6.0883e-05 | 0.00018265 | 86215 | 0.00013669 | 0.00081972 | 0.00013669 | 0.00081972 | 6.6602e-14 | 3.994e-13 | 0.0034173 | 0.020493 | 0.0034173 | 0.020493 | 0.0041008 | 0.024592 | 0.0041008 | 0.024592
PNA-402 | c | 1D | DAPjm | 2-Way Meter - Electr | Premise Network Admin | DAPjm shall be able to send HAN device un-join request to 2-Way Meter - Electr | han_dev_un_join_cmd | cmd | 24x7 | x per ¦ ElectrMtr per ¦ REPi un-join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | down |  | x | PNA-393 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-REPi-un-join | 5 | 5 | 25 | 1 | 3.171e-08 | 3.171e-08 | 10320 | 0.00032725 | 0.00032725 | 0.00032725 | 0.00032725 | 2.2673e-10 | 2.2673e-10 | 0.0081811 | 0.0081811 | 0.0081811 | 0.0081811 | 0.0016362 | 0.0016362 | 0.0016362 | 0.0016362 | 30785 | 0.00097619 | 0.00097619 | 0.00097619 | 0.00097619 | 5.4366e-11 | 5.4366e-11 | 0.024405 | 0.024405 | 0.024405 | 0.024405 | 0.0048809 | 0.0048809 | 0.0048809 | 0.0048809 | 44140 | 0.0013997 | 0.0013997 | 0.0013997 | 0.0013997 | 9.6977e-10 | 9.6977e-10 | 0.034992 | 0.034992 | 0.034992 | 0.034992 | 0.0069984 | 0.0069984 | 0.0069984 | 0.0069984 | 24295 | 0.00077039 | 0.00077039 | 0.00077039 | 0.00077039 | 1.1942e-12 | 1.1942e-12 | 0.01926 | 0.01926 | 0.01926 | 0.01926 | 0.0038519 | 0.0038519 | 0.0038519 | 0.0038519 | 5385 | 0.00017076 | 0.00017076 | 0.00017076 | 0.00017076 | 8.3199e-14 | 8.3199e-14 | 0.0042689 | 0.0042689 | 0.0042689 | 0.0042689 | 0.00085379 | 0.00085379 | 0.00085379 | 0.00085379 | 114925 | 0.0036442 | 0.0036442 | 0.0036442 | 0.0036442 | 1.7756e-12 | 1.7756e-12 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.018221 | 0.018221 | 0.018221 | 0.018221
PNA-403 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Premise Network Admin | DAPjm shall be able to process & forward HAN device un-join request to 2-Way Meter - Gas | han_dev_un_join_cmd | cmd | 24x7 | x per ¦ GasMtr per ¦ REPi un-join request per year | > 98% | < 30 sec | 25 | request-year |  | X | X | down |  | x | PNA-393 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-REPi-un-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 9010 | 0.00028571 | 0.00028571 | 0.00028571 | 0.00028571 | 1.9795e-10 | 1.9795e-10 | 0.0071426 | 0.0071426 | 0.0071426 | 0.0071426 | 0.0085712 | 0.0085712 | 0.0085712 | 0.0085712 | 27230 | 0.00086346 | 0.00086346 | 0.00086346 | 0.00086346 | 4.8088e-11 | 4.8088e-11 | 0.021586 | 0.021586 | 0.021586 | 0.021586 | 0.025904 | 0.025904 | 0.025904 | 0.025904 | 35515 | 0.0011262 | 0.0011262 | 0.0011262 | 0.0011262 | 7.8027e-10 | 7.8027e-10 | 0.028154 | 0.028154 | 0.028154 | 0.028154 | 0.033785 | 0.033785 | 0.033785 | 0.033785 | 13790 | 0.00043728 | 0.00043728 | 0.00043728 | 0.00043728 | 6.7785e-13 | 6.7785e-13 | 0.010932 | 0.010932 | 0.010932 | 0.010932 | 0.013118 | 0.013118 | 0.013118 | 0.013118 | 2545 | 8.0701e-05 | 8.0701e-05 | 8.0701e-05 | 8.0701e-05 | 3.9321e-14 | 3.9321e-14 | 0.0020175 | 0.0020175 | 0.0020175 | 0.0020175 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 88090 | 0.0027933 | 0.0027933 | 0.0027933 | 0.0027933 | 1.361e-12 | 1.361e-12 | 0.069833 | 0.069833 | 0.069833 | 0.069833 | 0.083799 | 0.083799 | 0.083799 | 0.083799
PNA-404 | c | 5Ba | DAPjm | ESI - In Meter | Premise Network Admin | DAPjm shall be able to process & forward HAN device un-join request to ESI - In Meter | han_dev_un_join_cmd | cmd | 24x7 | x per ¦ ESIInMtr-with-HANdevice per ¦ REPi un-join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | down |  | x | PNA-393 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-with-HANdevice-REPi-un-join | 5 | 5 | 25 | 1 | 1.9026e-07 | 1.9026e-07 | 10320 | 0.0019635 | 0.0019635 | 0.0019635 | 0.0019635 | 1.3604e-09 | 1.3604e-09 | 0.049087 | 0.049087 | 0.049087 | 0.049087 | 0.0098174 | 0.0098174 | 0.0098174 | 0.0098174 | 30785 | 0.0058571 | 0.0058571 | 0.0058571 | 0.0058571 | 3.262e-10 | 3.262e-10 | 0.14643 | 0.14643 | 0.14643 | 0.14643 | 0.029286 | 0.029286 | 0.029286 | 0.029286 | 44140 | 0.008398 | 0.008398 | 0.008398 | 0.008398 | 5.8186e-09 | 5.8186e-09 | 0.20995 | 0.20995 | 0.20995 | 0.20995 | 0.04199 | 0.04199 | 0.04199 | 0.04199 | 24295 | 0.0046223 | 0.0046223 | 0.0046223 | 0.0046223 | 7.1653e-12 | 7.1653e-12 | 0.11556 | 0.11556 | 0.11556 | 0.11556 | 0.023112 | 0.023112 | 0.023112 | 0.023112 | 5385 | 0.0010245 | 0.0010245 | 0.0010245 | 0.0010245 | 4.9919e-13 | 4.9919e-13 | 0.025614 | 0.025614 | 0.025614 | 0.025614 | 0.0051227 | 0.0051227 | 0.0051227 | 0.0051227 | 114925 | 0.021865 | 0.021865 | 0.021865 | 0.021865 | 1.0654e-11 | 1.0654e-11 | 0.54664 | 0.54664 | 0.54664 | 0.54664 | 0.10933 | 0.10933 | 0.10933 | 0.10933
PNA-408 | c | 1Dw | DAPjm | 2-Way Meter - Water | Premise Network Admin | DAPjm shall be able to process & forward HAN device un-join request to 2-Way Meter - Water | han_dev_un_join_cmd | cmd | 24x7 | x per ¦ WaterMtr per ¦ REPi un-join request per year | > 98% | < 30 sec | 25 | request-year |  | X | X | down |  | x | PNA-393 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-REPi-un-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 6310 | 1.0004e-05 | 6.0027e-05 | 1.0004e-05 | 6.0027e-05 | 6.9316e-12 | 4.159e-11 | 0.00025011 | 0.0015007 | 0.00025011 | 0.0015007 | 0.00030013 | 0.0018008 | 0.00030013 | 0.0018008 | 19180 | 3.041e-05 | 0.00018246 | 3.041e-05 | 0.00018246 | 1.6936e-12 | 1.0162e-11 | 0.00076024 | 0.0045615 | 0.00076024 | 0.0045615 | 0.00091229 | 0.0054737 | 0.00091229 | 0.0054737 | 45475 | 7.21e-05 | 0.0005047 | 7.21e-05 | 0.0005047 | 4.9955e-11 | 3.4968e-10 | 0.0018025 | 0.012618 | 0.0018025 | 0.012618 | 0.002163 | 0.015141 | 0.002163 | 0.015141 | 13970 | 2.2149e-05 | 6.6448e-05 | 2.2149e-05 | 6.6448e-05 | 3.4335e-14 | 1.03e-13 | 0.00055373 | 0.0016612 | 0.00055373 | 0.0016612 | 0.00066448 | 0.0019934 | 0.00066448 | 0.0019934 | 1280 | 2.0294e-06 | 6.0883e-06 | 2.0294e-06 | 6.0883e-06 | 9.8881e-16 | 2.9664e-15 | 5.0736e-05 | 0.00015221 | 5.0736e-05 | 0.00015221 | 6.0883e-05 | 0.00018265 | 6.0883e-05 | 0.00018265 | 86215 | 0.00013669 | 0.00081972 | 0.00013669 | 0.00081972 | 6.6602e-14 | 3.994e-13 | 0.0034173 | 0.020493 | 0.0034173 | 0.020493 | 0.0041008 | 0.024592 | 0.0041008 | 0.024592
PNA-436 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device un-join request acknowlegement to DAPjm | han_dev_un_join_ack | ack | 24x7 | x per ¦ ElectrMtr per ¦ REPi un-join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | up |  | x | PNA-435 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-REPi-un-join | 5 | 5 | 25 | 1 | 3.171e-08 | 3.171e-08 | 10320 | 0.00032725 | 0.00032725 | 0.00032725 | 0.00032725 | 2.2673e-10 | 2.2673e-10 | 0.0081811 | 0.0081811 | 0.0081811 | 0.0081811 | 0.0016362 | 0.0016362 | 0.0016362 | 0.0016362 | 30785 | 0.00097619 | 0.00097619 | 0.00097619 | 0.00097619 | 5.4366e-11 | 5.4366e-11 | 0.024405 | 0.024405 | 0.024405 | 0.024405 | 0.0048809 | 0.0048809 | 0.0048809 | 0.0048809 | 44140 | 0.0013997 | 0.0013997 | 0.0013997 | 0.0013997 | 9.6977e-10 | 9.6977e-10 | 0.034992 | 0.034992 | 0.034992 | 0.034992 | 0.0069984 | 0.0069984 | 0.0069984 | 0.0069984 | 24295 | 0.00077039 | 0.00077039 | 0.00077039 | 0.00077039 | 1.1942e-12 | 1.1942e-12 | 0.01926 | 0.01926 | 0.01926 | 0.01926 | 0.0038519 | 0.0038519 | 0.0038519 | 0.0038519 | 5385 | 0.00017076 | 0.00017076 | 0.00017076 | 0.00017076 | 8.3199e-14 | 8.3199e-14 | 0.0042689 | 0.0042689 | 0.0042689 | 0.0042689 | 0.00085379 | 0.00085379 | 0.00085379 | 0.00085379 | 114925 | 0.0036442 | 0.0036442 | 0.0036442 | 0.0036442 | 1.7756e-12 | 1.7756e-12 | 0.091106 | 0.091106 | 0.091106 | 0.091106 | 0.018221 | 0.018221 | 0.018221 | 0.018221
PNA-437 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device un-join request acknowlegement to DAPjm | han_dev_un_join_ack | ack | 24x7 | x per ¦ GasMtr per ¦ REPi-Mtr-un-join-request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-435 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-REPi-Mtr-un-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 9010 | 0.00028571 | 0.00028571 | 0.00028571 | 0.00028571 | 1.9795e-10 | 1.9795e-10 | 0.0071426 | 0.0071426 | 0.0071426 | 0.0071426 | 0.0085712 | 0.0085712 | 0.0085712 | 0.0085712 | 27230 | 0.00086346 | 0.00086346 | 0.00086346 | 0.00086346 | 4.8088e-11 | 4.8088e-11 | 0.021586 | 0.021586 | 0.021586 | 0.021586 | 0.025904 | 0.025904 | 0.025904 | 0.025904 | 35515 | 0.0011262 | 0.0011262 | 0.0011262 | 0.0011262 | 7.8027e-10 | 7.8027e-10 | 0.028154 | 0.028154 | 0.028154 | 0.028154 | 0.033785 | 0.033785 | 0.033785 | 0.033785 | 13790 | 0.00043728 | 0.00043728 | 0.00043728 | 0.00043728 | 6.7785e-13 | 6.7785e-13 | 0.010932 | 0.010932 | 0.010932 | 0.010932 | 0.013118 | 0.013118 | 0.013118 | 0.013118 | 2545 | 8.0701e-05 | 8.0701e-05 | 8.0701e-05 | 8.0701e-05 | 3.9321e-14 | 3.9321e-14 | 0.0020175 | 0.0020175 | 0.0020175 | 0.0020175 | 0.002421 | 0.002421 | 0.002421 | 0.002421 | 88090 | 0.0027933 | 0.0027933 | 0.0027933 | 0.0027933 | 1.361e-12 | 1.361e-12 | 0.069833 | 0.069833 | 0.069833 | 0.069833 | 0.083799 | 0.083799 | 0.083799 | 0.083799
PNA-439 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device un-join request acknowledgements to DAPjm | han_dev_un_join_ack | ack | 24x7 | x per ¦ ESIInMtr-with-HANdevice per ¦ REPi un-join request per year | > 98% | < 5 sec | 25 | request-year |  | X | X | up |  | x | PNA-435 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-with-HANdevice-REPi-un-join | 5 | 5 | 25 | 1 | 1.9026e-07 | 1.9026e-07 | 10320 | 0.0019635 | 0.0019635 | 0.0019635 | 0.0019635 | 1.3604e-09 | 1.3604e-09 | 0.049087 | 0.049087 | 0.049087 | 0.049087 | 0.0098174 | 0.0098174 | 0.0098174 | 0.0098174 | 30785 | 0.0058571 | 0.0058571 | 0.0058571 | 0.0058571 | 3.262e-10 | 3.262e-10 | 0.14643 | 0.14643 | 0.14643 | 0.14643 | 0.029286 | 0.029286 | 0.029286 | 0.029286 | 44140 | 0.008398 | 0.008398 | 0.008398 | 0.008398 | 5.8186e-09 | 5.8186e-09 | 0.20995 | 0.20995 | 0.20995 | 0.20995 | 0.04199 | 0.04199 | 0.04199 | 0.04199 | 24295 | 0.0046223 | 0.0046223 | 0.0046223 | 0.0046223 | 7.1653e-12 | 7.1653e-12 | 0.11556 | 0.11556 | 0.11556 | 0.11556 | 0.023112 | 0.023112 | 0.023112 | 0.023112 | 5385 | 0.0010245 | 0.0010245 | 0.0010245 | 0.0010245 | 4.9919e-13 | 4.9919e-13 | 0.025614 | 0.025614 | 0.025614 | 0.025614 | 0.0051227 | 0.0051227 | 0.0051227 | 0.0051227 | 114925 | 0.021865 | 0.021865 | 0.021865 | 0.021865 | 1.0654e-11 | 1.0654e-11 | 0.54664 | 0.54664 | 0.54664 | 0.54664 | 0.10933 | 0.10933 | 0.10933 | 0.10933
PNA-442 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device un-join request acknowlegement to DAPjm | han_dev_un_join_ack | ack | 24x7 | x per ¦ WaterMtr per ¦ REPi un-join request per year | > 98% | < 30 sec | 25 | request-year |  | X | X | up |  | x | PNA-435 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-REPi-un-join | 30 | 30 | 25 | 1 | 3.171e-08 | 3.171e-08 | 6310 | 1.0004e-05 | 6.0027e-05 | 1.0004e-05 | 6.0027e-05 | 6.9316e-12 | 4.159e-11 | 0.00025011 | 0.0015007 | 0.00025011 | 0.0015007 | 0.00030013 | 0.0018008 | 0.00030013 | 0.0018008 | 19180 | 3.041e-05 | 0.00018246 | 3.041e-05 | 0.00018246 | 1.6936e-12 | 1.0162e-11 | 0.00076024 | 0.0045615 | 0.00076024 | 0.0045615 | 0.00091229 | 0.0054737 | 0.00091229 | 0.0054737 | 45475 | 7.21e-05 | 0.0005047 | 7.21e-05 | 0.0005047 | 4.9955e-11 | 3.4968e-10 | 0.0018025 | 0.012618 | 0.0018025 | 0.012618 | 0.002163 | 0.015141 | 0.002163 | 0.015141 | 13970 | 2.2149e-05 | 6.6448e-05 | 2.2149e-05 | 6.6448e-05 | 3.4335e-14 | 1.03e-13 | 0.00055373 | 0.0016612 | 0.00055373 | 0.0016612 | 0.00066448 | 0.0019934 | 0.00066448 | 0.0019934 | 1280 | 2.0294e-06 | 6.0883e-06 | 2.0294e-06 | 6.0883e-06 | 9.8881e-16 | 2.9664e-15 | 5.0736e-05 | 0.00015221 | 5.0736e-05 | 0.00015221 | 6.0883e-05 | 0.00018265 | 6.0883e-05 | 0.00018265 | 86215 | 0.00013669 | 0.00081972 | 0.00013669 | 0.00081972 | 6.6602e-14 | 3.994e-13 | 0.0034173 | 0.020493 | 0.0034173 | 0.020493 | 0.0041008 | 0.024592 | 0.0041008 | 0.024592
PNA-478 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device join request cmd errors to the DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ElectrMtr-with-HANdevice-joins-REPi per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | up |  | x | PNA-477 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-with-HANdevice-joins-REPi | 5 | 5 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 10320 | 5.9722e-06 | 3.5833e-05 | 5.9722e-06 | 3.5833e-05 | 4.1379e-12 | 2.4827e-11 | 0.00014931 | 0.00089583 | 0.00014931 | 0.00089583 | 2.9861e-05 | 0.00017917 | 2.9861e-05 | 0.00017917 | 30785 | 1.7815e-05 | 0.00010689 | 1.7815e-05 | 0.00010689 | 9.9219e-13 | 5.9531e-12 | 0.00044538 | 0.0026723 | 0.00044538 | 0.0026723 | 8.9077e-05 | 0.00053446 | 8.9077e-05 | 0.00053446 | 44140 | 2.5544e-05 | 0.00017881 | 2.5544e-05 | 0.00017881 | 1.7698e-11 | 1.2389e-10 | 0.0006386 | 0.0044702 | 0.0006386 | 0.0044702 | 0.00012772 | 0.00089404 | 0.00012772 | 0.00089404 | 24295 | 1.406e-05 | 4.2179e-05 | 1.406e-05 | 4.2179e-05 | 2.1795e-14 | 6.5384e-14 | 0.00035149 | 0.0010545 | 0.00035149 | 0.0010545 | 7.0298e-05 | 0.00021089 | 7.0298e-05 | 0.00021089 | 5385 | 3.1163e-06 | 9.349e-06 | 3.1163e-06 | 9.349e-06 | 1.5184e-15 | 4.5552e-15 | 7.7908e-05 | 0.00023372 | 7.7908e-05 | 0.00023372 | 1.5582e-05 | 4.6745e-05 | 1.5582e-05 | 4.6745e-05 | 114925 | 6.6508e-05 | 0.00037306 | 6.6508e-05 | 0.00037306 | 3.2405e-14 | 1.8177e-13 | 0.0016627 | 0.0093265 | 0.0016627 | 0.0093265 | 0.00033254 | 0.0018653 | 0.00033254 | 0.0018653
PNA-479 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ REPi join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-477 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-REPi-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 9010 | 5.2141e-06 | 3.1285e-05 | 5.2141e-06 | 3.1285e-05 | 3.6126e-12 | 2.1676e-11 | 0.00013035 | 0.00078212 | 0.00013035 | 0.00078212 | 0.00015642 | 0.00093854 | 0.00015642 | 0.00093854 | 27230 | 1.5758e-05 | 9.4549e-05 | 1.5758e-05 | 9.4549e-05 | 8.7761e-13 | 5.2657e-12 | 0.00039395 | 0.0023637 | 0.00039395 | 0.0023637 | 0.00047274 | 0.0028365 | 0.00047274 | 0.0028365 | 35515 | 2.0553e-05 | 0.00014387 | 2.0553e-05 | 0.00014387 | 1.424e-11 | 9.968e-11 | 0.00051382 | 0.0035967 | 0.00051382 | 0.0035967 | 0.00061658 | 0.0043161 | 0.00061658 | 0.0043161 | 13790 | 7.9803e-06 | 2.3941e-05 | 7.9803e-06 | 2.3941e-05 | 1.2371e-14 | 3.7112e-14 | 0.00019951 | 0.00059852 | 0.00019951 | 0.00059852 | 0.00023941 | 0.00071823 | 0.00023941 | 0.00071823 | 2545 | 1.4728e-06 | 4.4184e-06 | 1.4728e-06 | 4.4184e-06 | 7.176e-16 | 2.1528e-15 | 3.682e-05 | 0.00011046 | 3.682e-05 | 0.00011046 | 4.4184e-05 | 0.00013255 | 4.4184e-05 | 0.00013255 | 88090 | 5.0978e-05 | 0.00029806 | 5.0978e-05 | 0.00029806 | 2.4838e-14 | 1.4523e-13 | 0.0012745 | 0.0074515 | 0.0012745 | 0.0074515 | 0.0015293 | 0.0089418 | 0.0015293 | 0.0089418
PNA-481 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ESIInMtr-Mtr-with-HANdevice per ¦ REPi joins per day | > 98% | < 5 sec | 25 | day |  | X | X | up |  | x | PNA-477 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-Mtr-with-HANdevice-REPi-join | 5 | 5 | 25 | 1 | 6.9444e-08 | 6.9444e-08 | 10320 | 3.5833e-05 | 0.000215 | 3.5833e-05 | 0.000215 | 2.4827e-11 | 1.4896e-10 | 0.00089583 | 0.005375 | 0.00089583 | 0.005375 | 0.00017917 | 0.001075 | 0.00017917 | 0.001075 | 30785 | 0.00010689 | 0.00064135 | 0.00010689 | 0.00064135 | 5.9531e-12 | 3.5719e-11 | 0.0026723 | 0.016034 | 0.0026723 | 0.016034 | 0.00053446 | 0.0032068 | 0.00053446 | 0.0032068 | 44140 | 0.00015326 | 0.0010728 | 0.00015326 | 0.0010728 | 1.0619e-10 | 7.4333e-10 | 0.0038316 | 0.026821 | 0.0038316 | 0.026821 | 0.00076632 | 0.0053642 | 0.00076632 | 0.0053642 | 24295 | 8.4358e-05 | 0.00025307 | 8.4358e-05 | 0.00025307 | 1.3077e-13 | 3.923e-13 | 0.0021089 | 0.0063268 | 0.0021089 | 0.0063268 | 0.00042179 | 0.0012654 | 0.00042179 | 0.0012654 | 5385 | 1.8698e-05 | 5.6094e-05 | 1.8698e-05 | 5.6094e-05 | 9.1103e-15 | 2.7331e-14 | 0.00046745 | 0.0014023 | 0.00046745 | 0.0014023 | 9.349e-05 | 0.00028047 | 9.349e-05 | 0.00028047 | 114925 | 0.00039905 | 0.0022384 | 0.00039905 | 0.0022384 | 1.9443e-13 | 1.0906e-12 | 0.0099761 | 0.055959 | 0.0099761 | 0.055959 | 0.0019952 | 0.011192 | 0.0019952 | 0.011192
PNA-484 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device join request cmd errors to DAPjm | han_dev_join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ WaterMtr-with-HANdevice per ¦ REPi join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-477 |  |  | 0.041667 | 1 | ESIInMtr | WaterMtr-with-HANdevice-REPi-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 6310 | 3.6516e-06 | 2.191e-05 | 3.6516e-06 | 2.191e-05 | 2.53e-12 | 1.518e-11 | 9.1291e-05 | 0.00054774 | 9.1291e-05 | 0.00054774 | 0.00010955 | 0.00065729 | 0.00010955 | 0.00065729 | 19180 | 1.11e-05 | 6.6597e-05 | 1.11e-05 | 6.6597e-05 | 6.1816e-13 | 3.709e-12 | 0.00027749 | 0.0016649 | 0.00027749 | 0.0016649 | 0.00033299 | 0.0019979 | 0.00033299 | 0.0019979 | 45475 | 2.6317e-05 | 0.00018422 | 2.6317e-05 | 0.00018422 | 1.8234e-11 | 1.2763e-10 | 0.00065791 | 0.0046054 | 0.00065791 | 0.0046054 | 0.0007895 | 0.0055265 | 0.0007895 | 0.0055265 | 13970 | 8.0845e-06 | 2.4253e-05 | 8.0845e-06 | 2.4253e-05 | 1.2532e-14 | 3.7597e-14 | 0.00020211 | 0.00060634 | 0.00020211 | 0.00060634 | 0.00024253 | 0.0007276 | 0.00024253 | 0.0007276 | 1280 | 3.7037e-08 | 2.2222e-06 | 3.7037e-08 | 2.2222e-06 | 1.8046e-17 | 1.0827e-15 | 9.2593e-07 | 5.5556e-05 | 9.2593e-07 | 5.5556e-05 | 1.1111e-06 | 6.6667e-05 | 1.1111e-06 | 6.6667e-05 | 86215 | 2.4946e-06 | 0.0002992 | 2.4946e-06 | 0.0002992 | 1.2155e-15 | 1.4578e-13 | 6.2366e-05 | 0.00748 | 6.2366e-05 | 0.00748 | 7.4839e-05 | 0.008976 | 7.4839e-05 | 0.008976
PNA-520 | c | 1D | 2-Way Meter - Electr | DAPjm | Premise Network Admin | 2-Way Meter - Electr shall be able to send HAN device un-join request cmd errors to the DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ElectrMtr-with-HANdevice per ¦ REPi un-join request per day | > 98% | < 5 sec | 25 | request-day |  | X | X | up |  | x | PNA-519 |  |  | 0.041667 | 1 | ESIInMtr | ElectrMtr-with-HANdevice-REPi-un-join | 5 | 5 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 10320 | 0.00011944 | 0.00011944 | 0.00011944 | 0.00011944 | 8.2758e-11 | 8.2758e-11 | 0.0029861 | 0.0029861 | 0.0029861 | 0.0029861 | 0.00059722 | 0.00059722 | 0.00059722 | 0.00059722 | 30785 | 0.00035631 | 0.00035631 | 0.00035631 | 0.00035631 | 1.9844e-11 | 1.9844e-11 | 0.0089077 | 0.0089077 | 0.0089077 | 0.0089077 | 0.0017815 | 0.0017815 | 0.0017815 | 0.0017815 | 44140 | 0.00051088 | 0.00051088 | 0.00051088 | 0.00051088 | 3.5396e-10 | 3.5396e-10 | 0.012772 | 0.012772 | 0.012772 | 0.012772 | 0.0025544 | 0.0025544 | 0.0025544 | 0.0025544 | 24295 | 0.00028119 | 0.00028119 | 0.00028119 | 0.00028119 | 4.3589e-13 | 4.3589e-13 | 0.0070298 | 0.0070298 | 0.0070298 | 0.0070298 | 0.001406 | 0.001406 | 0.001406 | 0.001406 | 5385 | 6.2326e-05 | 6.2326e-05 | 6.2326e-05 | 6.2326e-05 | 3.0368e-14 | 3.0368e-14 | 0.0015582 | 0.0015582 | 0.0015582 | 0.0015582 | 0.00031163 | 0.00031163 | 0.00031163 | 0.00031163 | 114925 | 0.0013302 | 0.0013302 | 0.0013302 | 0.0013302 | 6.481e-13 | 6.481e-13 | 0.033254 | 0.033254 | 0.033254 | 0.033254 | 0.0066508 | 0.0066508 | 0.0066508 | 0.0066508
PNA-521 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Premise Network Admin | 2-Way Meter - Gas shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ GasMtr per ¦ REPi un-join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-519 |  |  | 0.041667 | 1 | ESIInMtr | GasMtr-REPi-un-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 9010 | 0.00010428 | 0.00010428 | 0.00010428 | 0.00010428 | 7.2252e-11 | 7.2252e-11 | 0.0026071 | 0.0026071 | 0.0026071 | 0.0026071 | 0.0031285 | 0.0031285 | 0.0031285 | 0.0031285 | 27230 | 0.00031516 | 0.00031516 | 0.00031516 | 0.00031516 | 1.7552e-11 | 1.7552e-11 | 0.0078791 | 0.0078791 | 0.0078791 | 0.0078791 | 0.0094549 | 0.0094549 | 0.0094549 | 0.0094549 | 35515 | 0.00041105 | 0.00041105 | 0.00041105 | 0.00041105 | 2.848e-10 | 2.848e-10 | 0.010276 | 0.010276 | 0.010276 | 0.010276 | 0.012332 | 0.012332 | 0.012332 | 0.012332 | 13790 | 0.00015961 | 0.00015961 | 0.00015961 | 0.00015961 | 2.4741e-13 | 2.4741e-13 | 0.0039902 | 0.0039902 | 0.0039902 | 0.0039902 | 0.0047882 | 0.0047882 | 0.0047882 | 0.0047882 | 2545 | 2.9456e-05 | 2.9456e-05 | 2.9456e-05 | 2.9456e-05 | 1.4352e-14 | 1.4352e-14 | 0.0007364 | 0.0007364 | 0.0007364 | 0.0007364 | 0.00088368 | 0.00088368 | 0.00088368 | 0.00088368 | 88090 | 0.0010196 | 0.0010196 | 0.0010196 | 0.0010196 | 4.9677e-13 | 4.9677e-13 | 0.025489 | 0.025489 | 0.025489 | 0.025489 | 0.030587 | 0.030587 | 0.030587 | 0.030587
PNA-523 | c | 5Ba | ESI - In Meter | DAPjm | Premise Network Admin | ESI - In Meter shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ ESIInMtr-Mtr-with-HANdevice per ¦ REPi un-joins per day | > 98% | < 5 sec | 25 | day |  | X | X | up |  | x | PNA-519 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-Mtr-with-HANdevice-REPi-un-join | 5 | 5 | 25 | 1 | 6.9444e-08 | 6.9444e-08 | 10320 | 0.00071667 | 0.00071667 | 0.00071667 | 0.00071667 | 4.9655e-10 | 4.9655e-10 | 0.017917 | 0.017917 | 0.017917 | 0.017917 | 0.0035833 | 0.0035833 | 0.0035833 | 0.0035833 | 30785 | 0.0021378 | 0.0021378 | 0.0021378 | 0.0021378 | 1.1906e-10 | 1.1906e-10 | 0.053446 | 0.053446 | 0.053446 | 0.053446 | 0.010689 | 0.010689 | 0.010689 | 0.010689 | 44140 | 0.0030653 | 0.0030653 | 0.0030653 | 0.0030653 | 2.1238e-09 | 2.1238e-09 | 0.076632 | 0.076632 | 0.076632 | 0.076632 | 0.015326 | 0.015326 | 0.015326 | 0.015326 | 24295 | 0.0016872 | 0.0016872 | 0.0016872 | 0.0016872 | 2.6153e-12 | 2.6153e-12 | 0.042179 | 0.042179 | 0.042179 | 0.042179 | 0.0084358 | 0.0084358 | 0.0084358 | 0.0084358 | 5385 | 0.00037396 | 0.00037396 | 0.00037396 | 0.00037396 | 1.8221e-13 | 1.8221e-13 | 0.009349 | 0.009349 | 0.009349 | 0.009349 | 0.0018698 | 0.0018698 | 0.0018698 | 0.0018698 | 114925 | 0.0079809 | 0.0079809 | 0.0079809 | 0.0079809 | 3.8886e-12 | 3.8886e-12 | 0.19952 | 0.19952 | 0.19952 | 0.19952 | 0.039905 | 0.039905 | 0.039905 | 0.039905
PNA-526 | c | 1Dw | 2-Way Meter - Water | DAPjm | Premise Network Admin | 2-Way Meter - Water shall be able to process & forward HAN device un-join request cmd errors to DAPjm | han_dev_un-join_cmd_err | cmd-err | 24x7 | 1 per 1000 per ¦ WaterMtr-with-HANdevice per ¦ REPi un-join request per day | > 98% | < 30 sec | 25 | request-day |  | X | X | up |  | x | PNA-519 |  |  | 0.041667 | 1 | WaterMtr | WaterMtr-with-HANdevice-REPi-un-join | 30 | 30 | 25 | 1 | 1.1574e-08 | 1.1574e-08 | 6310 | 3.6516e-06 | 2.191e-05 | 3.6516e-06 | 2.191e-05 | 2.53e-12 | 1.518e-11 | 9.1291e-05 | 0.00054774 | 9.1291e-05 | 0.00054774 | 0.00010955 | 0.00065729 | 0.00010955 | 0.00065729 | 19180 | 1.11e-05 | 6.6597e-05 | 1.11e-05 | 6.6597e-05 | 6.1816e-13 | 3.709e-12 | 0.00027749 | 0.0016649 | 0.00027749 | 0.0016649 | 0.00033299 | 0.0019979 | 0.00033299 | 0.0019979 | 45475 | 2.6317e-05 | 0.00018422 | 2.6317e-05 | 0.00018422 | 1.8234e-11 | 1.2763e-10 | 0.00065791 | 0.0046054 | 0.00065791 | 0.0046054 | 0.0007895 | 0.0055265 | 0.0007895 | 0.0055265 | 13970 | 8.0845e-06 | 2.4253e-05 | 8.0845e-06 | 2.4253e-05 | 1.2532e-14 | 3.7597e-14 | 0.00020211 | 0.00060634 | 0.00020211 | 0.00060634 | 0.00024253 | 0.0007276 | 0.00024253 | 0.0007276 | 1280 | 7.4074e-07 | 2.2222e-06 | 7.4074e-07 | 2.2222e-06 | 3.6092e-16 | 1.0827e-15 | 1.8519e-05 | 5.5556e-05 | 1.8519e-05 | 5.5556e-05 | 2.2222e-05 | 6.6667e-05 | 2.2222e-05 | 6.6667e-05 | 86215 | 4.9893e-05 | 0.0002992 | 4.9893e-05 | 0.0002992 | 2.431e-14 | 1.4578e-13 | 0.0012473 | 0.00748 | 0.0012473 | 0.00748 | 0.0014968 | 0.008976 | 0.0014968 | 0.008976
PP-009 | c | 1D | DAPjm | 2-Way Meter - Electr | PrePay | DAPjm shall be able to process & forward a meter config for prepay capability request to 2-Way Meter - Electr | prepay_meter_config_cmd | cmd | 7AM - 10PM | 1 per ¦ DAPjm-Utl-PrePay-ElectrMtr per ¦ Utl PrePay enrollment | > 98% | < 5 sec | 25 | request | N | X | X | down |  | x | PP-001 |  |  | 0.041667 | 1 | ElectrMtr | Utl-PrePay-ElectrMtr | 5 | 5 | 25 | 1 | 3.171e-09 | 1.9026e-08 | 6750 | 2.1404e-05 | 0.00012842 | 2.1404e-05 | 0.00012842 | 1.483e-11 | 8.8979e-11 | 0.0005351 | 0.0032106 | 0.0005351 | 0.0032106 | 0.00010702 | 0.00064212 | 0.00010702 | 0.00064212 | 20125 | 6.3816e-05 | 0.0003829 | 6.3816e-05 | 0.0003829 | 3.5541e-12 | 2.1324e-11 | 0.0015954 | 0.0095724 | 0.0015954 | 0.0095724 | 0.00031908 | 0.0019145 | 0.00031908 | 0.0019145 | 34900 | 0.00011067 | 0.000664 | 0.00011067 | 0.000664 | 7.6676e-11 | 4.6006e-10 | 0.0027667 | 0.0166 | 0.0027667 | 0.0166 | 0.00055334 | 0.00332 | 0.00055334 | 0.00332 | 20650 | 6.5481e-05 | 0.00039288 | 6.5481e-05 | 0.00039288 | 1.015e-13 | 6.0903e-13 | 0.001637 | 0.0098221 | 0.001637 | 0.0098221 | 0.0003274 | 0.0019644 | 0.0003274 | 0.0019644 | 4905 | 1.5554e-05 | 9.3322e-05 | 1.5554e-05 | 9.3322e-05 | 7.5783e-15 | 4.547e-14 | 0.00038884 | 0.002333 | 0.00038884 | 0.002333 | 7.7768e-05 | 0.00046661 | 7.7768e-05 | 0.00046661 | 87330 | 0.00027692 | 0.0016615 | 0.00027692 | 0.0016615 | 1.3493e-13 | 8.0956e-13 | 0.006923 | 0.041538 | 0.006923 | 0.041538 | 0.0013846 | 0.0083076 | 0.0013846 | 0.0083076
PP-100 | c | 5Ba | DAPjm | ESI - In Meter | PrePay | DAPjm shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - In Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 per ¦ ESIInMtr-REPi-PrePay-Mtr-with-IPD per ¦ month | > 98% | < 5 sec | 50 - 150 | month |  | X | X | down |  | x | PP-090 |  |  | 0.066667 | 1 | IPD | ESIInMtr-REPi-PrePay-Mtr-with-IPD | 5 | 5 | 150 | 1 | 1.5432e-05 | 1.5432e-05 | 18759.5 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 1.2035e-06 | 1.2035e-06 | 43.4248 | 43.4248 | 43.4248 | 43.4248 | 1.4475 | 1.4475 | 1.4475 | 1.4475 | 56554.75 | 0.87276 | 0.87276 | 0.87276 | 0.87276 | 2.9164e-07 | 2.9164e-07 | 130.9138 | 130.9138 | 130.9138 | 130.9138 | 4.3638 | 4.3638 | 4.3638 | 4.3638 | 110095.5 | 1.699 | 1.699 | 1.699 | 1.699 | 7.063e-06 | 7.063e-06 | 254.8507 | 254.8507 | 254.8507 | 254.8507 | 8.495 | 8.495 | 8.495 | 8.495 | 48410 | 0.74707 | 0.74707 | 0.74707 | 0.74707 | 6.9484e-09 | 6.9484e-09 | 112.0602 | 112.0602 | 112.0602 | 112.0602 | 3.7353 | 3.7353 | 3.7353 | 3.7353 | 8730 | 0.13472 | 0.13472 | 0.13472 | 0.13472 | 3.9385e-10 | 3.9385e-10 | 20.2083 | 20.2083 | 20.2083 | 20.2083 | 0.67361 | 0.67361 | 0.67361 | 0.67361 | 242549.75 | 3.7431 | 3.7431 | 3.7431 | 3.7431 | 1.0943e-08 | 1.0943e-08 | 561.4578 | 561.4578 | 561.4578 | 561.4578 | 18.7153 | 18.7153 | 18.7153 | 18.7153
PP-114 | c | 5Ba | DAPjm | ESI - In Meter | PrePay | DAPjm shall be able to process & forward any of the PrePay messages (~10 different types) to the ESI - In Meter | prepay_msg_[1of10]_resp-data | resp-data | 7AM - 10PM | 25 per ¦ ESIInMtr-REPi-PrePay-Mtr-with-CustEMS per ¦ month | > 98% | < 5 sec | 50 - 150 | month |  | X | X | down |  | x | PP-104 |  |  | 0.066667 | 1 | CustEMS | ESIInMtr-REPi-PrePay-Mtr-with-CustEMS | 5 | 5 | 150 | 1 | 1.5432e-05 | 1.5432e-05 | 3310.5 | 0.051088 | 0.051088 | 0.051088 | 0.051088 | 2.1238e-07 | 2.1238e-07 | 7.6632 | 7.6632 | 7.6632 | 7.6632 | 0.25544 | 0.25544 | 0.25544 | 0.25544 | 9980.25 | 0.15402 | 0.15402 | 0.15402 | 0.15402 | 5.1465e-08 | 5.1465e-08 | 23.1024 | 23.1024 | 23.1024 | 23.1024 | 0.77008 | 0.77008 | 0.77008 | 0.77008 | 5794.5 | 0.089421 | 0.089421 | 0.089421 | 0.089421 | 3.7174e-07 | 3.7174e-07 | 13.4132 | 13.4132 | 13.4132 | 13.4132 | 0.44711 | 0.44711 | 0.44711 | 0.44711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19085.25 | 0.29453 | 0.29453 | 0.29453 | 0.29453 | 8.6102e-10 | 8.6102e-10 | 44.1788 | 44.1788 | 44.1788 | 44.1788 | 1.4726 | 1.4726 | 1.4726 | 1.4726
PP-136 | c | 1D | DAPjm | 2-Way Meter - Electr | PrePay | DAPjm shall be able to process & forward a service switch operate request to 2-Way Meter - Electr | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ DAPjm-Utl-PrePay-ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | PP-127 |  |  | 0.083333 | 1 | ElectrMtr | Utl-PrePay-ElectrMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 6750 | 0.0039062 | 0.0039062 | 0.0039062 | 0.0039062 | 2.7065e-09 | 2.7065e-09 | 0.097656 | 0.097656 | 0.097656 | 0.097656 | 0.11719 | 0.11719 | 0.11719 | 0.11719 | 20125 | 0.011646 | 0.011646 | 0.011646 | 0.011646 | 6.4862e-10 | 6.4862e-10 | 0.29116 | 0.29116 | 0.29116 | 0.29116 | 0.34939 | 0.34939 | 0.34939 | 0.34939 | 34900 | 0.020197 | 0.020197 | 0.020197 | 0.020197 | 1.3993e-08 | 1.3993e-08 | 0.50492 | 0.50492 | 0.50492 | 0.50492 | 0.6059 | 0.6059 | 0.6059 | 0.6059 | 20650 | 0.01195 | 0.01195 | 0.01195 | 0.01195 | 1.8525e-11 | 1.8525e-11 | 0.29876 | 0.29876 | 0.29876 | 0.29876 | 0.35851 | 0.35851 | 0.35851 | 0.35851 | 4905 | 0.0028385 | 0.0028385 | 0.0028385 | 0.0028385 | 1.383e-12 | 1.383e-12 | 0.070964 | 0.070964 | 0.070964 | 0.070964 | 0.085156 | 0.085156 | 0.085156 | 0.085156 | 87330 | 0.050538 | 0.050538 | 0.050538 | 0.050538 | 2.4624e-11 | 2.4624e-11 | 1.2635 | 1.2635 | 1.2635 | 1.2635 | 1.5161 | 1.5161 | 1.5161 | 1.5161
PP-161 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to send service switch state data to DAPjm | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 per 1000 per ¦ PrePay-ElectrMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | PP-160 |  |  | 0.083333 | 1 | ElectrMtr | PrePay-ElectrMtr | 30 | 30 | 100 | 1 | 5.787e-07 | 5.787e-07 | 6750 | 0.0039062 | 0.0039062 | 0.0039062 | 0.0039062 | 1.0826e-08 | 1.0826e-08 | 0.39062 | 0.39062 | 0.39062 | 0.39062 | 0.11719 | 0.11719 | 0.11719 | 0.11719 | 20125 | 0.011646 | 0.011646 | 0.011646 | 0.011646 | 2.5945e-09 | 2.5945e-09 | 1.1646 | 1.1646 | 1.1646 | 1.1646 | 0.34939 | 0.34939 | 0.34939 | 0.34939 | 34900 | 0.020197 | 0.020197 | 0.020197 | 0.020197 | 5.5974e-08 | 5.5974e-08 | 2.0197 | 2.0197 | 2.0197 | 2.0197 | 0.6059 | 0.6059 | 0.6059 | 0.6059 | 20650 | 0.01195 | 0.01195 | 0.01195 | 0.01195 | 7.4099e-11 | 7.4099e-11 | 1.195 | 1.195 | 1.195 | 1.195 | 0.35851 | 0.35851 | 0.35851 | 0.35851 | 4905 | 0.0028385 | 0.0028385 | 0.0028385 | 0.0028385 | 5.5322e-12 | 5.5322e-12 | 0.28385 | 0.28385 | 0.28385 | 0.28385 | 0.085156 | 0.085156 | 0.085156 | 0.085156 | 87330 | 0.050538 | 0.050538 | 0.050538 | 0.050538 | 9.8496e-11 | 9.8496e-11 | 5.0538 | 5.0538 | 5.0538 | 5.0538 | 1.5161 | 1.5161 | 1.5161 | 1.5161
PP-172 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to send service switch operate acknowledgment to DAPjm | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 per 1000 per ¦ PrePay-ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | up |  | x | PP-171 |  |  | 0.083333 | 1 | ElectrMtr | PrePay-ElectrMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 6750 | 0.0003125 | 0.0003125 | 0.0003125 | 0.0003125 | 2.1652e-10 | 2.1652e-10 | 0.0078125 | 0.0078125 | 0.0078125 | 0.0078125 | 0.009375 | 0.009375 | 0.009375 | 0.009375 | 20125 | 0.00093171 | 0.00093171 | 0.00093171 | 0.00093171 | 5.189e-11 | 5.189e-11 | 0.023293 | 0.023293 | 0.023293 | 0.023293 | 0.027951 | 0.027951 | 0.027951 | 0.027951 | 34900 | 0.0016157 | 0.0016157 | 0.0016157 | 0.0016157 | 1.1195e-09 | 1.1195e-09 | 0.040394 | 0.040394 | 0.040394 | 0.040394 | 0.048472 | 0.048472 | 0.048472 | 0.048472 | 20650 | 0.00095602 | 0.00095602 | 0.00095602 | 0.00095602 | 1.482e-12 | 1.482e-12 | 0.0239 | 0.0239 | 0.0239 | 0.0239 | 0.028681 | 0.028681 | 0.028681 | 0.028681 | 4905 | 0.00022708 | 0.00022708 | 0.00022708 | 0.00022708 | 1.1064e-13 | 1.1064e-13 | 0.0056771 | 0.0056771 | 0.0056771 | 0.0056771 | 0.0068125 | 0.0068125 | 0.0068125 | 0.0068125 | 87330 | 0.0040431 | 0.0040431 | 0.0040431 | 0.0040431 | 1.9699e-12 | 1.9699e-12 | 0.10108 | 0.10108 | 0.10108 | 0.10108 | 0.12129 | 0.12129 | 0.12129 | 0.12129
PP-181 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to send service switch operate faillure to DAPjm | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 per 1000 per ¦ PrePay-ElectrMtr per ¦ SW oper per day | > 98% | < 30 sec | 50 | day |  | X | X | up |  | x | PP-180 |  |  | 0.083333 | 1 | ElectrMtr | PrePay-ElectrMtr-SW-oper | 30 | 30 | 50 | 1 | 5.787e-10 | 5.787e-10 | 6750 | 3.9063e-06 | 3.9063e-06 | 3.9063e-06 | 3.9063e-06 | 5.4129e-12 | 5.4129e-12 | 0.00019531 | 0.00019531 | 0.00019531 | 0.00019531 | 0.00011719 | 0.00011719 | 0.00011719 | 0.00011719 | 20125 | 1.1646e-05 | 1.1646e-05 | 1.1646e-05 | 1.1646e-05 | 1.2972e-12 | 1.2972e-12 | 0.00058232 | 0.00058232 | 0.00058232 | 0.00058232 | 0.00034939 | 0.00034939 | 0.00034939 | 0.00034939 | 34900 | 2.0197e-05 | 2.0197e-05 | 2.0197e-05 | 2.0197e-05 | 2.7987e-11 | 2.7987e-11 | 0.0010098 | 0.0010098 | 0.0010098 | 0.0010098 | 0.0006059 | 0.0006059 | 0.0006059 | 0.0006059 | 20650 | 1.195e-05 | 1.195e-05 | 1.195e-05 | 1.195e-05 | 3.7049e-14 | 3.7049e-14 | 0.00059751 | 0.00059751 | 0.00059751 | 0.00059751 | 0.00035851 | 0.00035851 | 0.00035851 | 0.00035851 | 4905 | 2.8385e-06 | 2.8385e-06 | 2.8385e-06 | 2.8385e-06 | 2.7661e-15 | 2.7661e-15 | 0.00014193 | 0.00014193 | 0.00014193 | 0.00014193 | 8.5156e-05 | 8.5156e-05 | 8.5156e-05 | 8.5156e-05 | 87330 | 5.0538e-05 | 5.0538e-05 | 5.0538e-05 | 5.0538e-05 | 4.9248e-14 | 4.9248e-14 | 0.0025269 | 0.0025269 | 0.0025269 | 0.0025269 | 0.0015161 | 0.0015161 | 0.0015161 | 0.0015161
PP-190 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to report & send metrology information after a successful service switch operate to DAPjm | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 per 1000 per ¦ PrePay-ElectrMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | PP-189 |  |  | 0.083333 | 1 | ElectrMtr | PrePay-ElectrMtr | 30 | 30 | 100 | 1 | 4.6296e-08 | 4.6296e-08 | 6750 | 0.0003125 | 0.0003125 | 0.0003125 | 0.0003125 | 8.6607e-10 | 8.6607e-10 | 0.03125 | 0.03125 | 0.03125 | 0.03125 | 0.009375 | 0.009375 | 0.009375 | 0.009375 | 20125 | 0.00093171 | 0.00093171 | 0.00093171 | 0.00093171 | 2.0756e-10 | 2.0756e-10 | 0.093171 | 0.093171 | 0.093171 | 0.093171 | 0.027951 | 0.027951 | 0.027951 | 0.027951 | 34900 | 0.0016157 | 0.0016157 | 0.0016157 | 0.0016157 | 4.4779e-09 | 4.4779e-09 | 0.16157 | 0.16157 | 0.16157 | 0.16157 | 0.048472 | 0.048472 | 0.048472 | 0.048472 | 20650 | 0.00095602 | 0.00095602 | 0.00095602 | 0.00095602 | 5.9279e-12 | 5.9279e-12 | 0.095602 | 0.095602 | 0.095602 | 0.095602 | 0.028681 | 0.028681 | 0.028681 | 0.028681 | 4905 | 0.00022708 | 0.00022708 | 0.00022708 | 0.00022708 | 4.4257e-13 | 4.4257e-13 | 0.022708 | 0.022708 | 0.022708 | 0.022708 | 0.0068125 | 0.0068125 | 0.0068125 | 0.0068125 | 87330 | 0.0040431 | 0.0040431 | 0.0040431 | 0.0040431 | 7.8797e-12 | 7.8797e-12 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.12129 | 0.12129 | 0.12129 | 0.12129
PP-206 | c | 1D | DAPjm | 2-Way Meter - Electr | PrePay | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Electr | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ Utl-PrePay-ElectrMtr per ¦ day | > 98% | < 5 sec | 25 | day |  | X | X | down |  | x | PP-198 |  |  | 0.066667 | 1 | ElectrMtr | Utl-PrePay-ElectrMtr | 5 | 5 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 6750 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 2.1652e-09 | 2.1652e-09 | 0.078125 | 0.078125 | 0.078125 | 0.078125 | 0.015625 | 0.015625 | 0.015625 | 0.015625 | 20125 | 0.0093171 | 0.0093171 | 0.0093171 | 0.0093171 | 5.189e-10 | 5.189e-10 | 0.23293 | 0.23293 | 0.23293 | 0.23293 | 0.046586 | 0.046586 | 0.046586 | 0.046586 | 34900 | 0.016157 | 0.016157 | 0.016157 | 0.016157 | 1.1195e-08 | 1.1195e-08 | 0.40394 | 0.40394 | 0.40394 | 0.40394 | 0.080787 | 0.080787 | 0.080787 | 0.080787 | 20650 | 0.0095602 | 0.0095602 | 0.0095602 | 0.0095602 | 1.482e-11 | 1.482e-11 | 0.239 | 0.239 | 0.239 | 0.239 | 0.047801 | 0.047801 | 0.047801 | 0.047801 | 4905 | 0.0022708 | 0.0022708 | 0.0022708 | 0.0022708 | 1.1064e-12 | 1.1064e-12 | 0.056771 | 0.056771 | 0.056771 | 0.056771 | 0.011354 | 0.011354 | 0.011354 | 0.011354 | 87330 | 0.040431 | 0.040431 | 0.040431 | 0.040431 | 1.9699e-11 | 1.9699e-11 | 1.0108 | 1.0108 | 1.0108 | 1.0108 | 0.20215 | 0.20215 | 0.20215 | 0.20215
PP-224 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 1 per ¦ PrePay-ElectrMtr per ¦ on-demand Mtr read request | > 98% | < 5 sec | 100 | request |  | X | X | up |  | x | PP-223 |  |  | 0.066667 | 1 | ElectrMtr | PrePay-ElectrMtr-on-demand-Mtr-Read | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 6750 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 8.6607e-09 | 8.6607e-09 | 0.3125 | 0.3125 | 0.3125 | 0.3125 | 0.015625 | 0.015625 | 0.015625 | 0.015625 | 20125 | 0.0093171 | 0.0093171 | 0.0093171 | 0.0093171 | 2.0756e-09 | 2.0756e-09 | 0.93171 | 0.93171 | 0.93171 | 0.93171 | 0.046586 | 0.046586 | 0.046586 | 0.046586 | 34900 | 0.016157 | 0.016157 | 0.016157 | 0.016157 | 4.4779e-08 | 4.4779e-08 | 1.6157 | 1.6157 | 1.6157 | 1.6157 | 0.080787 | 0.080787 | 0.080787 | 0.080787 | 20650 | 0.0095602 | 0.0095602 | 0.0095602 | 0.0095602 | 5.9279e-11 | 5.9279e-11 | 0.95602 | 0.95602 | 0.95602 | 0.95602 | 0.047801 | 0.047801 | 0.047801 | 0.047801 | 4905 | 0.0022708 | 0.0022708 | 0.0022708 | 0.0022708 | 4.4257e-12 | 4.4257e-12 | 0.22708 | 0.22708 | 0.22708 | 0.22708 | 0.011354 | 0.011354 | 0.011354 | 0.011354 | 87330 | 0.040431 | 0.040431 | 0.040431 | 0.040431 | 7.8797e-11 | 7.8797e-11 | 4.0431 | 4.0431 | 4.0431 | 4.0431 | 0.20215 | 0.20215 | 0.20215 | 0.20215
PP-243 | c | 1D | 2-Way Meter - Electr | DAPjm | PrePay | 2-Way Meter - Electr shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ PrePay-ElectrMtr per ¦ x on-demand Mtr read cmd per day | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | PP-242 |  |  | 0.066667 | 1 | ElectrMtr | PrePay-ElectrMtr-on-demand-Mtr-Read | 5 | 5 | 50 | 1 | 4.6296e-10 | 4.6296e-10 | 6750 | 3.125e-06 | 3.125e-06 | 3.125e-06 | 3.125e-06 | 4.3303e-12 | 4.3303e-12 | 0.00015625 | 0.00015625 | 0.00015625 | 0.00015625 | 1.5625e-05 | 1.5625e-05 | 1.5625e-05 | 1.5625e-05 | 20125 | 9.3171e-06 | 9.3171e-06 | 9.3171e-06 | 9.3171e-06 | 1.0378e-12 | 1.0378e-12 | 0.00046586 | 0.00046586 | 0.00046586 | 0.00046586 | 4.6586e-05 | 4.6586e-05 | 4.6586e-05 | 4.6586e-05 | 34900 | 1.6157e-05 | 1.6157e-05 | 1.6157e-05 | 1.6157e-05 | 2.2389e-11 | 2.2389e-11 | 0.00080787 | 0.00080787 | 0.00080787 | 0.00080787 | 8.0787e-05 | 8.0787e-05 | 8.0787e-05 | 8.0787e-05 | 20650 | 9.5602e-06 | 9.5602e-06 | 9.5602e-06 | 9.5602e-06 | 2.9639e-14 | 2.9639e-14 | 0.00047801 | 0.00047801 | 0.00047801 | 0.00047801 | 4.7801e-05 | 4.7801e-05 | 4.7801e-05 | 4.7801e-05 | 4905 | 2.2708e-06 | 2.2708e-06 | 2.2708e-06 | 2.2708e-06 | 2.2129e-15 | 2.2129e-15 | 0.00011354 | 0.00011354 | 0.00011354 | 0.00011354 | 1.1354e-05 | 1.1354e-05 | 1.1354e-05 | 1.1354e-05 | 87330 | 4.0431e-05 | 4.0431e-05 | 4.0431e-05 | 4.0431e-05 | 3.9398e-14 | 3.9398e-14 | 0.0020215 | 0.0020215 | 0.0020215 | 0.0020215 | 0.00020215 | 0.00020215 | 0.00020215 | 0.00020215
PP-282 | c | 1Dg | DAPjm | 2-Way Meter - Gas | PrePay | DAPjm shall be able to forward a scheduled cancel valve operate request to 2-Way Meter - Gas | valve_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 per 1000 per ¦ Utl-PrePay-GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | PP-274 |  |  | 0.083333 | 1 | GasMtr | Utl-PrePay-GasMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 9010 | 0.00041713 | 0.00041713 | 0.00041713 | 0.00041713 | 2.8901e-10 | 2.8901e-10 | 0.010428 | 0.010428 | 0.010428 | 0.010428 | 0.012514 | 0.012514 | 0.012514 | 0.012514 | 27230 | 0.0012606 | 0.0012606 | 0.0012606 | 0.0012606 | 7.0209e-11 | 7.0209e-11 | 0.031516 | 0.031516 | 0.031516 | 0.031516 | 0.037819 | 0.037819 | 0.037819 | 0.037819 | 35515 | 0.0016442 | 0.0016442 | 0.0016442 | 0.0016442 | 1.1392e-09 | 1.1392e-09 | 0.041105 | 0.041105 | 0.041105 | 0.041105 | 0.049326 | 0.049326 | 0.049326 | 0.049326 | 13790 | 0.00063843 | 0.00063843 | 0.00063843 | 0.00063843 | 9.8966e-13 | 9.8966e-13 | 0.015961 | 0.015961 | 0.015961 | 0.015961 | 0.019153 | 0.019153 | 0.019153 | 0.019153 | 2545 | 0.00011782 | 0.00011782 | 0.00011782 | 0.00011782 | 5.7408e-14 | 5.7408e-14 | 0.0029456 | 0.0029456 | 0.0029456 | 0.0029456 | 0.0035347 | 0.0035347 | 0.0035347 | 0.0035347 | 88090 | 0.0040782 | 0.0040782 | 0.0040782 | 0.0040782 | 1.9871e-12 | 1.9871e-12 | 0.10196 | 0.10196 | 0.10196 | 0.10196 | 0.12235 | 0.12235 | 0.12235 | 0.12235
PP-291 | c | 1Dg | DAPjm | 2-Way Meter - Gas | PrePay | DAPjm shall be able to forward a valve operate request to 2-Way Meter - Gas | valve_opr_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ Utl-PrePay-GasMtr per ¦ day | > 98% | < 1 min | 25 | day |  | X | X | down |  | x | PP-283 |  |  | 0.083333 | 1 | GasMtr | Utl-PrePay-GasMtr | 60 | 60 | 25 | 1 | 5.787e-07 | 5.787e-07 | 9010 | 0.0052141 | 0.0052141 | 0.0052141 | 0.0052141 | 3.6126e-09 | 3.6126e-09 | 0.13035 | 0.13035 | 0.13035 | 0.13035 | 0.31285 | 0.31285 | 0.31285 | 0.31285 | 27230 | 0.015758 | 0.015758 | 0.015758 | 0.015758 | 8.7761e-10 | 8.7761e-10 | 0.39395 | 0.39395 | 0.39395 | 0.39395 | 0.94549 | 0.94549 | 0.94549 | 0.94549 | 35515 | 0.020553 | 0.020553 | 0.020553 | 0.020553 | 1.424e-08 | 1.424e-08 | 0.51382 | 0.51382 | 0.51382 | 0.51382 | 1.2332 | 1.2332 | 1.2332 | 1.2332 | 13790 | 0.0079803 | 0.0079803 | 0.0079803 | 0.0079803 | 1.2371e-11 | 1.2371e-11 | 0.19951 | 0.19951 | 0.19951 | 0.19951 | 0.47882 | 0.47882 | 0.47882 | 0.47882 | 2545 | 0.0014728 | 0.0014728 | 0.0014728 | 0.0014728 | 7.176e-13 | 7.176e-13 | 0.03682 | 0.03682 | 0.03682 | 0.03682 | 0.088368 | 0.088368 | 0.088368 | 0.088368 | 88090 | 0.050978 | 0.050978 | 0.050978 | 0.050978 | 2.4838e-11 | 2.4838e-11 | 1.2745 | 1.2745 | 1.2745 | 1.2745 | 3.0587 | 3.0587 | 3.0587 | 3.0587
PP-300 | c | 1Dg | DAPjm | 2-Way Meter - Gas | PrePay | DAPjm shall be able to process & forward a value state request to 2-Way Meter - Gas | valve_state_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ Utl-PrePay-GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | PP-292 |  |  | 0.083333 | 1 | GasMtr | Utl-PrePay-GasMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 9010 | 0.0052141 | 0.0052141 | 0.0052141 | 0.0052141 | 3.6126e-09 | 3.6126e-09 | 0.13035 | 0.13035 | 0.13035 | 0.13035 | 0.15642 | 0.15642 | 0.15642 | 0.15642 | 27230 | 0.015758 | 0.015758 | 0.015758 | 0.015758 | 8.7761e-10 | 8.7761e-10 | 0.39395 | 0.39395 | 0.39395 | 0.39395 | 0.47274 | 0.47274 | 0.47274 | 0.47274 | 35515 | 0.020553 | 0.020553 | 0.020553 | 0.020553 | 1.424e-08 | 1.424e-08 | 0.51382 | 0.51382 | 0.51382 | 0.51382 | 0.61658 | 0.61658 | 0.61658 | 0.61658 | 13790 | 0.0079803 | 0.0079803 | 0.0079803 | 0.0079803 | 1.2371e-11 | 1.2371e-11 | 0.19951 | 0.19951 | 0.19951 | 0.19951 | 0.23941 | 0.23941 | 0.23941 | 0.23941 | 2545 | 0.0014728 | 0.0014728 | 0.0014728 | 0.0014728 | 7.176e-13 | 7.176e-13 | 0.03682 | 0.03682 | 0.03682 | 0.03682 | 0.044184 | 0.044184 | 0.044184 | 0.044184 | 88090 | 0.050978 | 0.050978 | 0.050978 | 0.050978 | 2.4838e-11 | 2.4838e-11 | 1.2745 | 1.2745 | 1.2745 | 1.2745 | 1.5293 | 1.5293 | 1.5293 | 1.5293
PP-316 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to send valve state data to DAPjm | valve_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 per 1000 per ¦ PrePay-GasMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | PP-315 |  |  | 0.083333 | 1 | GasMtr | PrePay-GasMtr | 30 | 30 | 100 | 1 | 5.787e-07 | 5.787e-07 | 9010 | 0.0052141 | 0.0052141 | 0.0052141 | 0.0052141 | 1.445e-08 | 1.445e-08 | 0.52141 | 0.52141 | 0.52141 | 0.52141 | 0.15642 | 0.15642 | 0.15642 | 0.15642 | 27230 | 0.015758 | 0.015758 | 0.015758 | 0.015758 | 3.5104e-09 | 3.5104e-09 | 1.5758 | 1.5758 | 1.5758 | 1.5758 | 0.47274 | 0.47274 | 0.47274 | 0.47274 | 35515 | 0.020553 | 0.020553 | 0.020553 | 0.020553 | 5.696e-08 | 5.696e-08 | 2.0553 | 2.0553 | 2.0553 | 2.0553 | 0.61658 | 0.61658 | 0.61658 | 0.61658 | 13790 | 0.0079803 | 0.0079803 | 0.0079803 | 0.0079803 | 4.9483e-11 | 4.9483e-11 | 0.79803 | 0.79803 | 0.79803 | 0.79803 | 0.23941 | 0.23941 | 0.23941 | 0.23941 | 2545 | 0.0014728 | 0.0014728 | 0.0014728 | 0.0014728 | 2.8704e-12 | 2.8704e-12 | 0.14728 | 0.14728 | 0.14728 | 0.14728 | 0.044184 | 0.044184 | 0.044184 | 0.044184 | 88090 | 0.050978 | 0.050978 | 0.050978 | 0.050978 | 9.9353e-11 | 9.9353e-11 | 5.0978 | 5.0978 | 5.0978 | 5.0978 | 1.5293 | 1.5293 | 1.5293 | 1.5293
PP-325 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to send valve operate acknowledgment to DAPjm | valve_opr_cmd_ack | ack | 8AM - 8PM | 1-2 per 1000 per ¦ PrePay-GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | up |  | x | PP-324 |  |  | 0.083333 | 1 | GasMtr | PrePay-GasMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 9010 | 0.00041713 | 0.00041713 | 0.00041713 | 0.00041713 | 2.8901e-10 | 2.8901e-10 | 0.010428 | 0.010428 | 0.010428 | 0.010428 | 0.012514 | 0.012514 | 0.012514 | 0.012514 | 27230 | 0.0012606 | 0.0012606 | 0.0012606 | 0.0012606 | 7.0209e-11 | 7.0209e-11 | 0.031516 | 0.031516 | 0.031516 | 0.031516 | 0.037819 | 0.037819 | 0.037819 | 0.037819 | 35515 | 0.0016442 | 0.0016442 | 0.0016442 | 0.0016442 | 1.1392e-09 | 1.1392e-09 | 0.041105 | 0.041105 | 0.041105 | 0.041105 | 0.049326 | 0.049326 | 0.049326 | 0.049326 | 13790 | 0.00063843 | 0.00063843 | 0.00063843 | 0.00063843 | 9.8966e-13 | 9.8966e-13 | 0.015961 | 0.015961 | 0.015961 | 0.015961 | 0.019153 | 0.019153 | 0.019153 | 0.019153 | 2545 | 0.00011782 | 0.00011782 | 0.00011782 | 0.00011782 | 5.7408e-14 | 5.7408e-14 | 0.0029456 | 0.0029456 | 0.0029456 | 0.0029456 | 0.0035347 | 0.0035347 | 0.0035347 | 0.0035347 | 88090 | 0.0040782 | 0.0040782 | 0.0040782 | 0.0040782 | 1.9871e-12 | 1.9871e-12 | 0.10196 | 0.10196 | 0.10196 | 0.10196 | 0.12235 | 0.12235 | 0.12235 | 0.12235
PP-334 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to send valve operate faillure to DAPjm | valve_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 per 1000 per ¦ PrePay-GasMtr per ¦ valve close oper per day | > 98% | < 1 min | 50 | day |  | X | X | up |  | x | PP-333 |  |  | 0.083333 | 1 | GasMtr | PrePay-GasMtr-valve-oper | 60 | 60 | 50 | 1 | 5.787e-10 | 5.787e-10 | 9010 | 5.2141e-06 | 5.2141e-06 | 5.2141e-06 | 5.2141e-06 | 7.2252e-12 | 7.2252e-12 | 0.00026071 | 0.00026071 | 0.00026071 | 0.00026071 | 0.00031285 | 0.00031285 | 0.00031285 | 0.00031285 | 27230 | 1.5758e-05 | 1.5758e-05 | 1.5758e-05 | 1.5758e-05 | 1.7552e-12 | 1.7552e-12 | 0.00078791 | 0.00078791 | 0.00078791 | 0.00078791 | 0.00094549 | 0.00094549 | 0.00094549 | 0.00094549 | 35515 | 2.0553e-05 | 2.0553e-05 | 2.0553e-05 | 2.0553e-05 | 2.848e-11 | 2.848e-11 | 0.0010276 | 0.0010276 | 0.0010276 | 0.0010276 | 0.0012332 | 0.0012332 | 0.0012332 | 0.0012332 | 13790 | 7.9803e-06 | 7.9803e-06 | 7.9803e-06 | 7.9803e-06 | 2.4741e-14 | 2.4741e-14 | 0.00039902 | 0.00039902 | 0.00039902 | 0.00039902 | 0.00047882 | 0.00047882 | 0.00047882 | 0.00047882 | 2545 | 1.4728e-06 | 1.4728e-06 | 1.4728e-06 | 1.4728e-06 | 1.4352e-15 | 1.4352e-15 | 7.364e-05 | 7.364e-05 | 7.364e-05 | 7.364e-05 | 8.8368e-05 | 8.8368e-05 | 8.8368e-05 | 8.8368e-05 | 88090 | 5.0978e-05 | 5.0978e-05 | 5.0978e-05 | 5.0978e-05 | 4.9677e-14 | 4.9677e-14 | 0.0025489 | 0.0025489 | 0.0025489 | 0.0025489 | 0.0030587 | 0.0030587 | 0.0030587 | 0.0030587
PP-343 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to report & send metrology information after a successful valve operate to DAPjm | valve_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 per 1000 per ¦ PrePay-GasMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | PP-342 |  |  | 0.083333 | 1 | GasMtr | PrePay-GasMtr | 30 | 30 | 100 | 1 | 4.6296e-08 | 4.6296e-08 | 9010 | 0.00041713 | 0.00041713 | 0.00041713 | 0.00041713 | 1.156e-09 | 1.156e-09 | 0.041713 | 0.041713 | 0.041713 | 0.041713 | 0.012514 | 0.012514 | 0.012514 | 0.012514 | 27230 | 0.0012606 | 0.0012606 | 0.0012606 | 0.0012606 | 2.8084e-10 | 2.8084e-10 | 0.12606 | 0.12606 | 0.12606 | 0.12606 | 0.037819 | 0.037819 | 0.037819 | 0.037819 | 35515 | 0.0016442 | 0.0016442 | 0.0016442 | 0.0016442 | 4.5568e-09 | 4.5568e-09 | 0.16442 | 0.16442 | 0.16442 | 0.16442 | 0.049326 | 0.049326 | 0.049326 | 0.049326 | 13790 | 0.00063843 | 0.00063843 | 0.00063843 | 0.00063843 | 3.9586e-12 | 3.9586e-12 | 0.063843 | 0.063843 | 0.063843 | 0.063843 | 0.019153 | 0.019153 | 0.019153 | 0.019153 | 2545 | 0.00011782 | 0.00011782 | 0.00011782 | 0.00011782 | 2.2963e-13 | 2.2963e-13 | 0.011782 | 0.011782 | 0.011782 | 0.011782 | 0.0035347 | 0.0035347 | 0.0035347 | 0.0035347 | 88090 | 0.0040782 | 0.0040782 | 0.0040782 | 0.0040782 | 7.9483e-12 | 7.9483e-12 | 0.40782 | 0.40782 | 0.40782 | 0.40782 | 0.12235 | 0.12235 | 0.12235 | 0.12235
PP-359 | c | 1Dg | DAPjm | 2-Way Meter - Gas | PrePay | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Gas | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ Utl-PrePay-GasMtr per ¦ day | > 98% | < 1 hr | 25 | day |  | X | X | down |  | x | PP-351 |  |  | 0.066667 | 1 | GasMtr | Utl-PrePay-GasMtr | 3600 | 3600 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 9010 | 0.0041713 | 0.0041713 | 0.0041713 | 0.0041713 | 2.8901e-09 | 2.8901e-09 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 15.0167 | 15.0167 | 15.0167 | 15.0167 | 27230 | 0.012606 | 0.012606 | 0.012606 | 0.012606 | 7.0209e-10 | 7.0209e-10 | 0.31516 | 0.31516 | 0.31516 | 0.31516 | 45.3833 | 45.3833 | 45.3833 | 45.3833 | 35515 | 0.016442 | 0.016442 | 0.016442 | 0.016442 | 1.1392e-08 | 1.1392e-08 | 0.41105 | 0.41105 | 0.41105 | 0.41105 | 59.1917 | 59.1917 | 59.1917 | 59.1917 | 13790 | 0.0063843 | 0.0063843 | 0.0063843 | 0.0063843 | 9.8966e-12 | 9.8966e-12 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 22.9833 | 22.9833 | 22.9833 | 22.9833 | 2545 | 0.0011782 | 0.0011782 | 0.0011782 | 0.0011782 | 5.7408e-13 | 5.7408e-13 | 0.029456 | 0.029456 | 0.029456 | 0.029456 | 4.2417 | 4.2417 | 4.2417 | 4.2417 | 88090 | 0.040782 | 0.040782 | 0.040782 | 0.040782 | 1.9871e-11 | 1.9871e-11 | 1.0196 | 1.0196 | 1.0196 | 1.0196 | 146.8167 | 146.8167 | 146.8167 | 146.8167
PP-372 | c | 1Dw | DAPjm | 2-Way Meter - Water | PrePay | DAPjm shall be able to process & forward on-demand meter read requests to the 2-Way Meter - Water | on-demand_Mtr-read_cmd | cmd | 7AM - 10PM | 25 per 1000 per ¦ Utl-PrePay-WaterMtr per ¦ day | > 98% | < 1 hr | 25 | day |  | X | X | down |  | x | PP-364 |  |  | 0.066667 | 1 | WaterMtr | Utl-PrePay-WaterMtr | 3600 | 3600 | 25 | 1 | 4.6296e-07 | 4.6296e-07 | 6310 | 0.0029213 | 0.0029213 | 0.0029213 | 0.0029213 | 2.024e-09 | 2.024e-09 | 0.073032 | 0.073032 | 0.073032 | 0.073032 | 10.5167 | 10.5167 | 10.5167 | 10.5167 | 19180 | 0.0088796 | 0.0088796 | 0.0088796 | 0.0088796 | 4.9453e-10 | 4.9453e-10 | 0.22199 | 0.22199 | 0.22199 | 0.22199 | 31.9667 | 31.9667 | 31.9667 | 31.9667 | 45475 | 0.021053 | 0.021053 | 0.021053 | 0.021053 | 1.4587e-08 | 1.4587e-08 | 0.52633 | 0.52633 | 0.52633 | 0.52633 | 75.7917 | 75.7917 | 75.7917 | 75.7917 | 13970 | 0.0064676 | 0.0064676 | 0.0064676 | 0.0064676 | 1.0026e-11 | 1.0026e-11 | 0.16169 | 0.16169 | 0.16169 | 0.16169 | 23.2833 | 23.2833 | 23.2833 | 23.2833 | 1280 | 0.00059259 | 0.00059259 | 0.00059259 | 0.00059259 | 2.8873e-13 | 2.8873e-13 | 0.014815 | 0.014815 | 0.014815 | 0.014815 | 2.1333 | 2.1333 | 2.1333 | 2.1333 | 86215 | 0.039914 | 0.039914 | 0.039914 | 0.039914 | 1.9448e-11 | 1.9448e-11 | 0.99786 | 0.99786 | 0.99786 | 0.99786 | 143.6917 | 143.6917 | 143.6917 | 143.6917
PP-398 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 per 1000 per ¦ PrePay-GasMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | PP-397 |  |  | 0.066667 | 1 | GasMtr | PrePay-GasMtr | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 9010 | 0.0041713 | 0.0041713 | 0.0041713 | 0.0041713 | 1.156e-08 | 1.156e-08 | 0.41713 | 0.41713 | 0.41713 | 0.41713 | 0.020856 | 0.020856 | 0.020856 | 0.020856 | 27230 | 0.012606 | 0.012606 | 0.012606 | 0.012606 | 2.8084e-09 | 2.8084e-09 | 1.2606 | 1.2606 | 1.2606 | 1.2606 | 0.063032 | 0.063032 | 0.063032 | 0.063032 | 35515 | 0.016442 | 0.016442 | 0.016442 | 0.016442 | 4.5568e-08 | 4.5568e-08 | 1.6442 | 1.6442 | 1.6442 | 1.6442 | 0.082211 | 0.082211 | 0.082211 | 0.082211 | 13790 | 0.0063843 | 0.0063843 | 0.0063843 | 0.0063843 | 3.9586e-11 | 3.9586e-11 | 0.63843 | 0.63843 | 0.63843 | 0.63843 | 0.031921 | 0.031921 | 0.031921 | 0.031921 | 2545 | 0.0011782 | 0.0011782 | 0.0011782 | 0.0011782 | 2.2963e-12 | 2.2963e-12 | 0.11782 | 0.11782 | 0.11782 | 0.11782 | 0.0058912 | 0.0058912 | 0.0058912 | 0.0058912 | 88090 | 0.040782 | 0.040782 | 0.040782 | 0.040782 | 7.9483e-11 | 7.9483e-11 | 4.0782 | 4.0782 | 4.0782 | 4.0782 | 0.20391 | 0.20391 | 0.20391 | 0.20391
PP-413 | c | 1Dw | 2-Way Meter - Water | DAPjm | PrePay | 2-Way Meter - Water shall be able to send on-demand meter read data to DAPjm | on-demand_Mtr-read_resp-data | resp-data | 7AM - 10PM | 25 per 1000 per ¦ PrePay-WaterMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | PP-412 |  |  | 0.066667 | 1 | WaterMtr | PrePay-WaterMtr | 5 | 5 | 100 | 1 | 4.6296e-07 | 4.6296e-07 | 6310 | 0.0029213 | 0.0029213 | 0.0029213 | 0.0029213 | 8.0961e-09 | 8.0961e-09 | 0.29213 | 0.29213 | 0.29213 | 0.29213 | 0.014606 | 0.014606 | 0.014606 | 0.014606 | 19180 | 0.0088796 | 0.0088796 | 0.0088796 | 0.0088796 | 1.9781e-09 | 1.9781e-09 | 0.88796 | 0.88796 | 0.88796 | 0.88796 | 0.044398 | 0.044398 | 0.044398 | 0.044398 | 45475 | 0.021053 | 0.021053 | 0.021053 | 0.021053 | 5.8347e-08 | 5.8347e-08 | 2.1053 | 2.1053 | 2.1053 | 2.1053 | 0.10527 | 0.10527 | 0.10527 | 0.10527 | 13970 | 0.0064676 | 0.0064676 | 0.0064676 | 0.0064676 | 4.0103e-11 | 4.0103e-11 | 0.64676 | 0.64676 | 0.64676 | 0.64676 | 0.032338 | 0.032338 | 0.032338 | 0.032338 | 1280 | 0.00059259 | 0.00059259 | 0.00059259 | 0.00059259 | 1.1549e-12 | 1.1549e-12 | 0.059259 | 0.059259 | 0.059259 | 0.059259 | 0.002963 | 0.002963 | 0.002963 | 0.002963 | 86215 | 0.039914 | 0.039914 | 0.039914 | 0.039914 | 7.7791e-11 | 7.7791e-11 | 3.9914 | 3.9914 | 3.9914 | 3.9914 | 0.19957 | 0.19957 | 0.19957 | 0.19957
PP-495 | c | 1Dg | 2-Way Meter - Gas | DAPjm | PrePay | 2-Way Meter - Gas shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ PrePay-GasMtr per ¦ x on-demand Mtr read cmd | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | PP-494 |  |  | 0.066667 | 1 | GasMtr | PrePay-GasMtr-on-demand-Mtr-read | 5 | 5 | 50 | 1 | 4.6296e-10 | 4.6296e-10 | 9010 | 4.1713e-06 | 4.1713e-06 | 4.1713e-06 | 4.1713e-06 | 5.7802e-12 | 5.7802e-12 | 0.00020856 | 0.00020856 | 0.00020856 | 0.00020856 | 2.0856e-05 | 2.0856e-05 | 2.0856e-05 | 2.0856e-05 | 27230 | 1.2606e-05 | 1.2606e-05 | 1.2606e-05 | 1.2606e-05 | 1.4042e-12 | 1.4042e-12 | 0.00063032 | 0.00063032 | 0.00063032 | 0.00063032 | 6.3032e-05 | 6.3032e-05 | 6.3032e-05 | 6.3032e-05 | 35515 | 1.6442e-05 | 1.6442e-05 | 1.6442e-05 | 1.6442e-05 | 2.2784e-11 | 2.2784e-11 | 0.00082211 | 0.00082211 | 0.00082211 | 0.00082211 | 8.2211e-05 | 8.2211e-05 | 8.2211e-05 | 8.2211e-05 | 13790 | 6.3843e-06 | 6.3843e-06 | 6.3843e-06 | 6.3843e-06 | 1.9793e-14 | 1.9793e-14 | 0.00031921 | 0.00031921 | 0.00031921 | 0.00031921 | 3.1921e-05 | 3.1921e-05 | 3.1921e-05 | 3.1921e-05 | 2545 | 1.1782e-06 | 1.1782e-06 | 1.1782e-06 | 1.1782e-06 | 1.1482e-15 | 1.1482e-15 | 5.8912e-05 | 5.8912e-05 | 5.8912e-05 | 5.8912e-05 | 5.8912e-06 | 5.8912e-06 | 5.8912e-06 | 5.8912e-06 | 88090 | 4.0782e-05 | 4.0782e-05 | 4.0782e-05 | 4.0782e-05 | 3.9741e-14 | 3.9741e-14 | 0.0020391 | 0.0020391 | 0.0020391 | 0.0020391 | 0.00020391 | 0.00020391 | 0.00020391 | 0.00020391
PP-509 | c | 1Dw | 2-Way Meter - Water | DAPjm | PrePay | 2-Way Meter - Water shall be able to report & forward Meter on-demand read request app errors to DAPjm | on-demand_Mtr-read_cmd_err | cmd-err | 7AM - 10PM | 1 per ¦ PrePay-WaterMtr per ¦ x on-demand Mtr read cmd | > 98% | < 5 sec | 50 | cmd |  | X | X | up |  | x | PP-508 |  |  | 0.066667 | 1 | WaterMtr | PrePay-WaterMtr-on-demand-Mtr-Read | 5 | 5 | 50 | 1 | 4.6296e-10 | 4.6296e-10 | 6310 | 2.9213e-06 | 2.9213e-06 | 2.9213e-06 | 2.9213e-06 | 4.0481e-12 | 4.0481e-12 | 0.00014606 | 0.00014606 | 0.00014606 | 0.00014606 | 1.4606e-05 | 1.4606e-05 | 1.4606e-05 | 1.4606e-05 | 19180 | 8.8796e-06 | 8.8796e-06 | 8.8796e-06 | 8.8796e-06 | 9.8906e-13 | 9.8906e-13 | 0.00044398 | 0.00044398 | 0.00044398 | 0.00044398 | 4.4398e-05 | 4.4398e-05 | 4.4398e-05 | 4.4398e-05 | 45475 | 2.1053e-05 | 2.1053e-05 | 2.1053e-05 | 2.1053e-05 | 2.9174e-11 | 2.9174e-11 | 0.0010527 | 0.0010527 | 0.0010527 | 0.0010527 | 0.00010527 | 0.00010527 | 0.00010527 | 0.00010527 | 13970 | 6.4676e-06 | 6.4676e-06 | 6.4676e-06 | 6.4676e-06 | 2.0051e-14 | 2.0051e-14 | 0.00032338 | 0.00032338 | 0.00032338 | 0.00032338 | 3.2338e-05 | 3.2338e-05 | 3.2338e-05 | 3.2338e-05 | 1280 | 5.9259e-07 | 5.9259e-07 | 5.9259e-07 | 5.9259e-07 | 5.7747e-16 | 5.7747e-16 | 2.963e-05 | 2.963e-05 | 2.963e-05 | 2.963e-05 | 2.963e-06 | 2.963e-06 | 2.963e-06 | 2.963e-06 | 86215 | 3.9914e-05 | 3.9914e-05 | 3.9914e-05 | 3.9914e-05 | 3.8895e-14 | 3.8895e-14 | 0.0019957 | 0.0019957 | 0.0019957 | 0.0019957 | 0.00019957 | 0.00019957 | 0.00019957 | 0.00019957
PR-0754 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Critical Peak Pricing data-on-exception to the 2-Way Meter - Electr | CPP_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-CPP-ElectrMtr per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | PR-0745 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-CPP-ElectrMtr | 5 | 5 | 100 | 1 |  | 6.9444e-07 | 20640 |  | 0.014333 |  | 0.014333 |  | 3.9724e-08 |  | 1.4333 |  | 1.4333 |  | 0.071667 |  | 0.071667 | 61570 |  | 0.042757 |  | 0.042757 |  | 9.525e-09 |  | 4.2757 |  | 4.2757 |  | 0.21378 |  | 0.21378 | 88280 |  | 0.061306 |  | 0.061306 |  | 1.699e-07 |  | 6.1306 |  | 6.1306 |  | 0.30653 |  | 0.30653 | 24295 |  | 0.016872 |  | 0.016872 |  | 1.0461e-10 |  | 1.6872 |  | 1.6872 |  | 0.084358 |  | 0.084358 | 5385 |  | 0.0037396 |  | 0.0037396 |  | 7.2882e-12 |  | 0.37396 |  | 0.37396 |  | 0.018698 |  | 0.018698 | 200170 |  | 0.13901 |  | 0.13901 |  | 2.7092e-10 |  | 13.9007 |  | 13.9007 | 0 | 0.69503 | 0 | 0.69503
PR-0755 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Critical Peak Pricing data-on-exception to ESI - In Meter | CPP_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-CPP-ESIInMtr-with-HANdevice per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | PR-0745 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-CPP-ESIInMtr-with-HANdevice | 5 | 5 | 100 | 1 |  | 4.1667e-06 | 20640 |  | 0.086 |  | 0.086 |  | 2.3834e-07 |  | 8.6 |  | 8.6 |  | 0.43 |  | 0.43 | 61570 |  | 0.25654 |  | 0.25654 |  | 5.715e-08 |  | 25.6542 |  | 25.6542 |  | 1.2827 |  | 1.2827 | 88280 |  | 0.36783 |  | 0.36783 |  | 1.0194e-06 |  | 36.7833 |  | 36.7833 |  | 1.8392 |  | 1.8392 | 24295 |  | 0.10123 |  | 0.10123 |  | 6.2768e-10 |  | 10.1229 |  | 10.1229 |  | 0.50615 |  | 0.50615 | 5385 |  | 0.022437 |  | 0.022437 |  | 4.3729e-11 |  | 2.2437 |  | 2.2437 |  | 0.11219 |  | 0.11219 | 200170 |  | 0.83404 |  | 0.83404 |  | 1.6255e-09 |  | 83.4042 |  | 83.4042 | 0 | 4.1702 | 0 | 4.1702
PR-0788 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Critical Peak Pricing data broadcast request to the 2-Way Meter - Electr | CPP_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-CPP-ElectrMtr per ¦ LMS - REPi CPP price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  |  | X | down |  | x | PR-0779 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data broadcast event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
PR-0789 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Critical Peak Pricing data broadcast request to ESI - In Meter | CPP_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-CPP-ESIInMtr per ¦ LMS - REPi CPP price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  |  | X | down |  | x | PR-0779 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data broadcast event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
PR-0822 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Critical Peak Pricing data multicast request to the 2-Way Meter - Electr | CPP_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-CPP-ElectrMtr per ¦ LMS - REPi CPP price data multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | PR-0813 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data multicast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 3096 |  | 0.035833 |  | 0.035833 |  | 9.9309e-08 |  | 3.5833 |  | 3.5833 |  | 0.17917 |  | 0.17917 | 9235.5 |  | 0.10689 |  | 0.10689 |  | 2.3812e-08 |  | 10.6892 |  | 10.6892 |  | 0.53446 |  | 0.53446 | 13242 |  | 0.15326 |  | 0.15326 |  | 4.2476e-07 |  | 15.3264 |  | 15.3264 |  | 0.76632 |  | 0.76632 | 3644.25 |  | 0.042179 |  | 0.042179 |  | 2.6153e-10 |  | 4.2179 |  | 4.2179 |  | 0.21089 |  | 0.21089 | 807.75 |  | 0.009349 |  | 0.009349 |  | 1.8221e-11 |  | 0.9349 |  | 0.9349 |  | 0.046745 |  | 0.046745 | 30025.5 |  | 0.34752 |  | 0.34752 |  | 6.7729e-10 |  | 34.7517 |  | 34.7517 | 0 | 1.7376 | 0 | 1.7376
PR-0823 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Critical Peak Pricing data multicast request to ESI - In Meter | CPP_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-CPP-ESIInMtr per ¦ LMS - REPi CPP price data multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | PR-0813 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-CPP-ESIInMtr_LMS - REPi CPP price data multicast request event | 5 | 5 | 100 | 1 |  | 6.9444e-05 | 3096 |  | 0.215 |  | 0.215 |  | 5.9585e-07 |  | 21.5 |  | 21.5 |  | 1.075 |  | 1.075 | 9235.5 |  | 0.64135 |  | 0.64135 |  | 1.4287e-07 |  | 64.1354 |  | 64.1354 |  | 3.2068 |  | 3.2068 | 13242 |  | 0.91958 |  | 0.91958 |  | 2.5485e-06 |  | 91.9583 |  | 91.9583 |  | 4.5979 |  | 4.5979 | 3644.25 |  | 0.25307 |  | 0.25307 |  | 1.5692e-09 |  | 25.3073 |  | 25.3073 |  | 1.2654 |  | 1.2654 | 807.75 |  | 0.056094 |  | 0.056094 |  | 1.0932e-10 |  | 5.6094 |  | 5.6094 |  | 0.28047 |  | 0.28047 | 30025.5 |  | 2.0851 |  | 2.0851 |  | 4.0638e-09 |  | 208.5104 |  | 208.5104 | 0 | 10.4255 | 0 | 10.4255
PR-0848 | c | 1D | 2-Way Meter - Electr | DAPjm | Price | 2-Way Meter - Electr shall be able to send Critical Peak Pricing data acknowlegements to the DAPjm | CPP_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-REPi-joined-CPP-ElectrMtr per ¦ LMS - REPi CPP price data event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | PR-0847 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-CPP-ElectrMtr_LMS - REPi CPP price data event | 5 | 5 | 25 | 1 |  | 1.1574e-05 | 10320 |  | 0.11944 |  | 0.11944 |  | 8.2758e-08 |  | 2.9861 |  | 2.9861 |  | 0.59722 |  | 0.59722 | 30785 |  | 0.35631 |  | 0.35631 |  | 1.9844e-08 |  | 8.9077 |  | 8.9077 |  | 1.7815 |  | 1.7815 | 44140 |  | 0.51088 |  | 0.51088 |  | 3.5396e-07 |  | 12.772 |  | 12.772 |  | 2.5544 |  | 2.5544 | 12147.5 |  | 0.1406 |  | 0.1406 |  | 2.1795e-10 |  | 3.5149 |  | 3.5149 |  | 0.70298 |  | 0.70298 | 2692.5 |  | 0.031163 |  | 0.031163 |  | 1.5184e-11 |  | 0.77908 |  | 0.77908 |  | 0.15582 |  | 0.15582 | 100085 |  | 1.1584 |  | 1.1584 |  | 5.6441e-10 |  | 28.9598 |  | 28.9598 | 0 | 5.792 | 0 | 5.792
PR-0851 | c | 5Ba | ESI - In Meter | DAPjm | Price | ESI - In Meter shall be able to process & forward Critical Peak Pricing data acknowledgements to DAPjm | CPP_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-ESIInMtr-REPi-joined-CPP-HANdevice per ¦ LMS - REPi CPP price data event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | PR-0847 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-CPP-HANdevice_LMS - REPi CPP price data event | 5 | 5 | 25 | 1 |  | 6.9444e-05 | 10320 |  | 0.71667 |  | 0.71667 |  | 4.9655e-07 |  | 17.9167 |  | 17.9167 |  | 3.5833 |  | 3.5833 | 30785 |  | 2.1378 |  | 2.1378 |  | 1.1906e-07 |  | 53.4462 |  | 53.4462 |  | 10.6892 |  | 10.6892 | 44140 |  | 3.0653 |  | 3.0653 |  | 2.1238e-06 |  | 76.6319 |  | 76.6319 |  | 15.3264 |  | 15.3264 | 12147.5 |  | 0.84358 |  | 0.84358 |  | 1.3077e-09 |  | 21.0894 |  | 21.0894 |  | 4.2179 |  | 4.2179 | 2692.5 |  | 0.18698 |  | 0.18698 |  | 9.1103e-11 |  | 4.6745 |  | 4.6745 |  | 0.9349 |  | 0.9349 | 100085 |  | 6.9503 |  | 6.9503 |  | 3.3865e-09 |  | 173.7587 |  | 173.7587 | 0 | 34.7517 | 0 | 34.7517
PR-0890 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Time of Use price data-on-exception to the 2-Way Meter - Electr | TOU_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-TOU-ElectrMtr per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | PR-0881 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-TOU-ElectrMtr | 5 | 5 | 100 | 1 |  | 6.9444e-07 | 206400 |  | 0.14333 |  | 0.14333 |  | 3.9724e-07 |  | 14.3333 |  | 14.3333 |  | 0.71667 |  | 0.71667 | 615700 |  | 0.42757 |  | 0.42757 |  | 9.525e-08 |  | 42.7569 |  | 42.7569 |  | 2.1378 |  | 2.1378 | 882800 |  | 0.61306 |  | 0.61306 |  | 1.699e-06 |  | 61.3056 |  | 61.3056 |  | 3.0653 |  | 3.0653 | 485900 |  | 0.33743 |  | 0.33743 |  | 2.0923e-09 |  | 33.7431 |  | 33.7431 |  | 1.6872 |  | 1.6872 | 107700 |  | 0.074792 |  | 0.074792 |  | 1.4576e-10 |  | 7.4792 |  | 7.4792 |  | 0.37396 |  | 0.37396 | 2298500 |  | 1.5962 |  | 1.5962 |  | 3.1109e-09 |  | 159.6181 |  | 159.6181 | 0 | 7.9809 | 0 | 7.9809
PR-0891 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Time of Use price data-on-exception to ESI - In Meter | TOU_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-TOU-ESIInMtr-with-HANdevice per ¦ day | > 98% | < 5 sec | 100 | day |  |  | X | down |  | x | PR-0881 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-TOU-ESIInMtr-with-HANdevice | 5 | 5 | 100 | 1 |  | 4.1667e-06 | 206400 |  | 0.86 |  | 0.86 |  | 2.3834e-06 |  | 86 |  | 86 |  | 4.3 |  | 4.3 | 615700 |  | 2.5654 |  | 2.5654 |  | 5.715e-07 |  | 256.5417 |  | 256.5417 |  | 12.8271 |  | 12.8271 | 882800 |  | 3.6783 |  | 3.6783 |  | 1.0194e-05 |  | 367.8333 |  | 367.8333 |  | 18.3917 |  | 18.3917 | 485900 |  | 2.0246 |  | 2.0246 |  | 1.2554e-08 |  | 202.4583 |  | 202.4583 |  | 10.1229 |  | 10.1229 | 107700 |  | 0.44875 |  | 0.44875 |  | 8.7459e-10 |  | 44.875 |  | 44.875 |  | 2.2437 |  | 2.2437 | 2298500 |  | 9.5771 |  | 9.5771 |  | 1.8665e-08 |  | 957.7083 |  | 957.7083 | 0 | 47.8854 | 0 | 47.8854
PR-0924 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Time of Use price data broadcast request to the 2-Way Meter - Electr | TOU_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-TOU-ElectrMtr per ¦ LMS - REPi TOU price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  |  | X | down |  | x | PR-0915 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data broadcast event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.5784e-12 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 3.2077e-11 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 7.1766e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 |  | 5.787e-05 |  | 5.787e-05 | 1 |  | 1.1574e-05 |  | 1.1574e-05 |  | 2.2557e-14 |  | 0.0011574 |  | 0.0011574 | 0 | 5.787e-05 | 0 | 5.787e-05
PR-0925 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Time of Use price data broadcast request to ESI - In Meter | TOU_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-TOU-ESIInMtr per ¦ LMS - REPi TOU price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  |  | X | down |  | x | PR-0915 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data broadcast event | 5 | 5 | 100 | 1 |  | 6.9444e-05 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 1.9246e-10 |  | 0.0069444 |  | 0.0069444 |  | 0.00034722 |  | 0.00034722 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 1.547e-11 |  | 0.0069444 |  | 0.0069444 |  | 0.00034722 |  | 0.00034722 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 1.9246e-10 |  | 0.0069444 |  | 0.0069444 |  | 0.00034722 |  | 0.00034722 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 4.306e-13 |  | 0.0069444 |  | 0.0069444 |  | 0.00034722 |  | 0.00034722 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 1.3534e-13 |  | 0.0069444 |  | 0.0069444 |  | 0.00034722 |  | 0.00034722 | 1 |  | 6.9444e-05 |  | 6.9444e-05 |  | 1.3534e-13 |  | 0.0069444 |  | 0.0069444 | 0 | 0.00034722 | 0 | 0.00034722
PR-0958 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Time of Use price data multicast request to the 2-Way Meter - Electr | TOU_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-TOU-ElectrMtr per ¦ LMS - REPi TOU price data multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | PR-0949 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-TOU-ElectrMtrLMS - REPi TOU price data multicast request event | 5 | 5 | 100 | 1 |  | 1.1574e-05 | 30960 |  | 0.35833 |  | 0.35833 |  | 9.9309e-07 |  | 35.8333 |  | 35.8333 |  | 1.7917 |  | 1.7917 | 92355 |  | 1.0689 |  | 1.0689 |  | 2.3812e-07 |  | 106.8924 |  | 106.8924 |  | 5.3446 |  | 5.3446 | 132420 |  | 1.5326 |  | 1.5326 |  | 4.2476e-06 |  | 153.2639 |  | 153.2639 |  | 7.6632 |  | 7.6632 | 72885 |  | 0.84358 |  | 0.84358 |  | 5.2307e-09 |  | 84.3576 |  | 84.3576 |  | 4.2179 |  | 4.2179 | 16155 |  | 0.18698 |  | 0.18698 |  | 3.6441e-10 |  | 18.6979 |  | 18.6979 |  | 0.9349 |  | 0.9349 | 344775 |  | 3.9905 |  | 3.9905 |  | 7.7772e-09 |  | 399.0451 |  | 399.0451 | 0 | 19.9523 | 0 | 19.9523
PR-0959 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Time of Use price data multicast request to ESI - In Meter | TOU_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-TOU-ESIInMtr per ¦ LMS - REPi TOU price data multicast request event | > 98% | < 5 sec | 100 | event |  |  | X | down |  | x | PR-0949 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-TOU-ESIInMtr_LMS - REPi TOU price data multicast request event | 5 | 5 | 100 | 1 |  | 6.9444e-05 | 30960 |  | 2.15 |  | 2.15 |  | 5.9585e-06 |  | 215 |  | 215 |  | 10.75 |  | 10.75 | 92355 |  | 6.4135 |  | 6.4135 |  | 1.4287e-06 |  | 641.3542 |  | 641.3542 |  | 32.0677 |  | 32.0677 | 132420 |  | 9.1958 |  | 9.1958 |  | 2.5485e-05 |  | 919.5833 |  | 919.5833 |  | 45.9792 |  | 45.9792 | 72885 |  | 5.0615 |  | 5.0615 |  | 3.1384e-08 |  | 506.1458 |  | 506.1458 |  | 25.3073 |  | 25.3073 | 16155 |  | 1.1219 |  | 1.1219 |  | 2.1865e-09 |  | 112.1875 |  | 112.1875 |  | 5.6094 |  | 5.6094 | 344775 |  | 23.9427 |  | 23.9427 |  | 4.6663e-08 |  | 2394.2708 |  | 2394.2708 | 0 | 119.7135 | 0 | 119.7135
PR-0984 | c | 1D | 2-Way Meter - Electr | DAPjm | Price | 2-Way Meter - Electr shall be able to send Time of Use price data acknowlegements to the DAPjm | TOU_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-REPi-joined-TOU-ElectrMtr per ¦ LMS - REPi TOU price data event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | PR-0983 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-TOU-ElectrMtr_LMS - REPi TOU price data event | 5 | 5 | 25 | 1 |  | 1.1574e-05 | 103200 |  | 1.1944 |  | 1.1944 |  | 8.2758e-07 |  | 29.8611 |  | 29.8611 |  | 5.9722 |  | 5.9722 | 307850 |  | 3.5631 |  | 3.5631 |  | 1.9844e-07 |  | 89.077 |  | 89.077 |  | 17.8154 |  | 17.8154 | 441400 |  | 5.1088 |  | 5.1088 |  | 3.5396e-06 |  | 127.7199 |  | 127.7199 |  | 25.544 |  | 25.544 | 242950 |  | 2.8119 |  | 2.8119 |  | 4.3589e-09 |  | 70.298 |  | 70.298 |  | 14.0596 |  | 14.0596 | 53850 |  | 0.62326 |  | 0.62326 |  | 3.0368e-10 |  | 15.5816 |  | 15.5816 |  | 3.1163 |  | 3.1163 | 1149250 |  | 13.3015 |  | 13.3015 |  | 6.481e-09 |  | 332.5376 |  | 332.5376 | 0 | 66.5075 | 0 | 66.5075
PR-0987 | c | 5Ba | ESI - In Meter | DAPjm | Price | ESI - In Meter shall be able to process & forward Time of Use price data acknowledgements to DAPjm | TOU_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-ESIInMtr-REPi-joined-TOU-HANdevice per ¦ LMS - REPi TOU price data event | > 98% | < 5 sec | 25 | event |  |  | X | up |  | x | PR-0983 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-TOU-HANdevice_LMS - REPi TOU price data event | 5 | 5 | 25 | 1 |  | 6.9444e-05 | 103200 |  | 7.1667 |  | 7.1667 |  | 4.9655e-06 |  | 179.1667 |  | 179.1667 |  | 35.8333 |  | 35.8333 | 307850 |  | 21.3785 |  | 21.3785 |  | 1.1906e-06 |  | 534.4618 |  | 534.4618 |  | 106.8924 |  | 106.8924 | 441400 |  | 30.6528 |  | 30.6528 |  | 2.1238e-05 |  | 766.3194 |  | 766.3194 |  | 153.2639 |  | 153.2639 | 242950 |  | 16.8715 |  | 16.8715 |  | 2.6153e-08 |  | 421.7882 |  | 421.7882 |  | 84.3576 |  | 84.3576 | 53850 |  | 3.7396 |  | 3.7396 |  | 1.8221e-09 |  | 93.4896 |  | 93.4896 |  | 18.6979 |  | 18.6979 | 1149250 |  | 79.809 |  | 79.809 |  | 3.8886e-08 |  | 1995.2257 |  | 1995.2257 | 0 | 399.0451 | 0 | 399.0451
PR-1026 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Real Time Pricing data-on-exception to the 2-Way Meter - Electr | RTP_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-RTP-ElectrMtr per ¦ 6 per day | > 98% | < 5 sec | 100 | day |  | X | X | down |  | x | PR-1017 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-RTP-ElectrMtr | 5 | 5 | 100 | 1 | 4.1667e-06 | 4.1667e-06 | 10320 | 0.043 | 0.043 | 0.043 | 0.043 | 1.1917e-07 | 1.1917e-07 | 4.3 | 4.3 | 4.3 | 4.3 | 0.215 | 0.215 | 0.215 | 0.215 | 30785 | 0.12827 | 0.12827 | 0.12827 | 0.12827 | 2.8575e-08 | 2.8575e-08 | 12.8271 | 12.8271 | 12.8271 | 12.8271 | 0.64135 | 0.64135 | 0.64135 | 0.64135 | 44140 | 0.18392 | 0.18392 | 0.18392 | 0.18392 | 5.0971e-07 | 5.0971e-07 | 18.3917 | 18.3917 | 18.3917 | 18.3917 | 0.91958 | 0.91958 | 0.91958 | 0.91958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85245 | 0.35519 | 0.35519 | 0.35519 | 0.35519 | 6.9224e-10 | 6.9224e-10 | 35.5187 | 35.5187 | 35.5187 | 35.5187 | 1.7759 | 1.7759 | 1.7759 | 1.7759
PR-1027 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Real Time Pricing data-on-exception to ESI - In Meter | RTP_pricing-data_cmd | cmd | 24x7 | 60 per 1000 per ¦ DAPjm-REPi-joined-RTP-ESIInMtr-with-HANdevice per ¦ 6 per day | > 98% | < 5 sec | 100 | day |  | X | X | down |  | x | PR-1017 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-RTP-ESIInMtr-with-HANdevice | 5 | 5 | 100 | 1 | 2.5e-05 | 2.5e-05 | 10320 | 0.258 | 0.258 | 0.258 | 0.258 | 7.1502e-07 | 7.1502e-07 | 25.8 | 25.8 | 25.8 | 25.8 | 1.29 | 1.29 | 1.29 | 1.29 | 30785 | 0.76963 | 0.76963 | 0.76963 | 0.76963 | 1.7145e-07 | 1.7145e-07 | 76.9625 | 76.9625 | 76.9625 | 76.9625 | 3.8481 | 3.8481 | 3.8481 | 3.8481 | 44140 | 1.1035 | 1.1035 | 1.1035 | 1.1035 | 3.0583e-06 | 3.0583e-06 | 110.35 | 110.35 | 110.35 | 110.35 | 5.5175 | 5.5175 | 5.5175 | 5.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85245 | 2.1311 | 2.1311 | 2.1311 | 2.1311 | 4.1534e-09 | 4.1534e-09 | 213.1125 | 213.1125 | 213.1125 | 213.1125 | 10.6556 | 10.6556 | 10.6556 | 10.6556
PR-1060 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Real Time Pricing data broadcast request to the 2-Way Meter - Electr | RTP_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-RTP-ElectrMtr per ¦ LMS - REPi RTP price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  | X | X | down |  | x | PR-1051 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data broadcast event | 5 | 5 | 100 | 1 | 3.8052e-07 | 3.8052e-07 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 1.0546e-12 | 1.0546e-12 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 8.4768e-14 | 8.4768e-14 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 1.0546e-12 | 1.0546e-12 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 7.4161e-16 | 7.4161e-16 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06
PR-1061 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Real Time Pricing data broadcast request to ESI - In Meter | RTP_pricing-data_brdcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-RTP-ESIInMtr per ¦ LMS - REPi RTP price data broadcast event - 12 per year | > 98% | < 5 sec | 100 | event-year |  | X | X | down |  | x | PR-1051 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data broadcast event | 5 | 5 | 100 | 1 | 3.8052e-07 | 3.8052e-07 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 1.0546e-12 | 1.0546e-12 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 8.4768e-14 | 8.4768e-14 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 1.0546e-12 | 1.0546e-12 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 3.8052e-07 | 7.4161e-16 | 7.4161e-16 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 3.8052e-05 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06 | 1.9026e-06
PR-1094 | c | 1D | DAPjm | 2-Way Meter - Electr | Price | DAPjm shall be able to send Real Time Pricing data multicast request to the 2-Way Meter - Electr | RTP_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-RTP-ElectrMtr per ¦ LMS - REPi RTP price data multicast request event | > 98% | < 5 sec | 100 | event |  | X | X | down |  | x | PR-1085 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data multicast request event | 5 | 5 | 100 | 1 | 3.8052e-07 | 3.8052e-07 | 1548 | 0.00058904 | 0.00058904 | 0.00058904 | 0.00058904 | 1.6325e-09 | 1.6325e-09 | 0.058904 | 0.058904 | 0.058904 | 0.058904 | 0.0029452 | 0.0029452 | 0.0029452 | 0.0029452 | 4617.75 | 0.0017571 | 0.0017571 | 0.0017571 | 0.0017571 | 3.9144e-10 | 3.9144e-10 | 0.17571 | 0.17571 | 0.17571 | 0.17571 | 0.0087857 | 0.0087857 | 0.0087857 | 0.0087857 | 6621 | 0.0025194 | 0.0025194 | 0.0025194 | 0.0025194 | 6.9823e-09 | 6.9823e-09 | 0.25194 | 0.25194 | 0.25194 | 0.25194 | 0.012597 | 0.012597 | 0.012597 | 0.012597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12786.75 | 0.0048656 | 0.0048656 | 0.0048656 | 0.0048656 | 9.4828e-12 | 9.4828e-12 | 0.48656 | 0.48656 | 0.48656 | 0.48656 | 0.024328 | 0.024328 | 0.024328 | 0.024328
PR-1095 | c | 5Ba | DAPjm | ESI - In Meter | Price | DAPjm shall be able to process & forward Real Time Pricing data multicast request to ESI - In Meter | RTP_pricing-data_mltcst | cmd | 24x7 | 1 per ¦ DAPjm-REPi-joined-RTP-ESIInMtr per ¦ LMS - REPi RTP price data multicast request event | > 98% | < 5 sec | 100 | event |  | X | X | down |  | x | PR-1085 |  |  | 0.041667 | 6 | ESIInMtr | REPi-joined-RTP-ESIInMtr_LMS - REPi RTP price data multicast request event | 5 | 5 | 100 | 1 | 2.2831e-06 | 2.2831e-06 | 1548 | 0.0035342 | 0.0035342 | 0.0035342 | 0.0035342 | 9.7949e-09 | 9.7949e-09 | 0.35342 | 0.35342 | 0.35342 | 0.35342 | 0.017671 | 0.017671 | 0.017671 | 0.017671 | 4617.75 | 0.010543 | 0.010543 | 0.010543 | 0.010543 | 2.3486e-09 | 2.3486e-09 | 1.0543 | 1.0543 | 1.0543 | 1.0543 | 0.052714 | 0.052714 | 0.052714 | 0.052714 | 6621 | 0.015116 | 0.015116 | 0.015116 | 0.015116 | 4.1894e-08 | 4.1894e-08 | 1.5116 | 1.5116 | 1.5116 | 1.5116 | 0.075582 | 0.075582 | 0.075582 | 0.075582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12786.75 | 0.029193 | 0.029193 | 0.029193 | 0.029193 | 5.6897e-11 | 5.6897e-11 | 2.9193 | 2.9193 | 2.9193 | 2.9193 | 0.14597 | 0.14597 | 0.14597 | 0.14597
PR-1120 | c | 1D | 2-Way Meter - Electr | DAPjm | Price | 2-Way Meter - Electr shall be able to send Real Time Pricing data acknowlegements to the DAPjm | RTP_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-REPi-joined-RTP-ElectrMtr per ¦ LMS - REPi RTP price data event | > 98% | < 5 sec | 25 | event |  | X | X | up |  | x | PR-1119 |  |  | 0.041667 | 1 | ESIInMtr | REPi-joined-RTP-ElectrMtr_LMS - REPi RTP price data event | 5 | 5 | 25 | 1 | 6.9444e-05 | 6.9444e-05 | 9288 | 0.645 | 0.645 | 0.645 | 0.645 | 4.4689e-07 | 4.4689e-07 | 16.125 | 16.125 | 16.125 | 16.125 | 3.225 | 3.225 | 3.225 | 3.225 | 27706.5 | 1.9241 | 1.9241 | 1.9241 | 1.9241 | 1.0716e-07 | 1.0716e-07 | 48.1016 | 48.1016 | 48.1016 | 48.1016 | 9.6203 | 9.6203 | 9.6203 | 9.6203 | 35312 | 2.4522 | 2.4522 | 2.4522 | 2.4522 | 1.699e-06 | 1.699e-06 | 61.3056 | 61.3056 | 61.3056 | 61.3056 | 12.2611 | 12.2611 | 12.2611 | 12.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72306.5 | 5.0213 | 5.0213 | 5.0213 | 5.0213 | 2.4466e-09 | 2.4466e-09 | 125.5321 | 125.5321 | 125.5321 | 125.5321 | 25.1064 | 25.1064 | 25.1064 | 25.1064
PR-1123 | c | 5Ba | ESI - In Meter | DAPjm | Price | ESI - In Meter shall be able to process & forward Real Time Pricing data acknowledgements to DAPjm | RTP_pricing-data_ack | ack | 24x7 | x per 1000 per ¦ DAPjm-ESIInMtr-REPi-joined-RTP-HANdevice per ¦ LMS - REPi RTP price data event | > 98% | < 5 sec | 25 | event |  | X | X | up |  | x | PR-1119 |  |  | 0.041667 | 6 | ESIInMtr | ESIInMtr-REPi-joined-RTP-HANdevice_LMS - REPi RTP price data event | 5 | 5 | 25 | 1 | 0.00041667 | 0.00041667 | 9288 | 3.87 | 3.87 | 3.87 | 3.87 | 2.6813e-06 | 2.6813e-06 | 96.75 | 96.75 | 96.75 | 96.75 | 19.35 | 19.35 | 19.35 | 19.35 | 27706.5 | 11.5444 | 11.5444 | 11.5444 | 11.5444 | 6.4294e-07 | 6.4294e-07 | 288.6094 | 288.6094 | 288.6094 | 288.6094 | 57.7219 | 57.7219 | 57.7219 | 57.7219 | 35312 | 14.7133 | 14.7133 | 14.7133 | 14.7133 | 1.0194e-05 | 1.0194e-05 | 367.8333 | 367.8333 | 367.8333 | 367.8333 | 73.5667 | 73.5667 | 73.5667 | 73.5667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72306.5 | 30.1277 | 30.1277 | 30.1277 | 30.1277 | 1.4679e-08 | 1.4679e-08 | 753.1927 | 753.1927 | 753.1927 | 753.1927 | 150.6385 | 150.6385 | 150.6385 | 150.6385
SS-026 | c | 1D | DAPjm | 2-Way Meter - Electr | Service Switch | DAPjm shall be able to forward a scheduled cancel service switch operate request to 2-Way Meter - Electr | SW_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-001 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 206400 | 0.0095556 | 0.0095556 | 0.0095556 | 0.0095556 | 6.6206e-09 | 6.6206e-09 | 0.23889 | 0.23889 | 0.23889 | 0.23889 | 0.28667 | 0.28667 | 0.28667 | 0.28667 | 615700 | 0.028505 | 0.028505 | 0.028505 | 0.028505 | 1.5875e-09 | 1.5875e-09 | 0.71262 | 0.71262 | 0.71262 | 0.71262 | 0.85514 | 0.85514 | 0.85514 | 0.85514 | 882800 | 0.04087 | 0.04087 | 0.04087 | 0.04087 | 2.8317e-08 | 2.8317e-08 | 1.0218 | 1.0218 | 1.0218 | 1.0218 | 1.2261 | 1.2261 | 1.2261 | 1.2261 | 485900 | 0.022495 | 0.022495 | 0.022495 | 0.022495 | 3.4871e-11 | 3.4871e-11 | 0.56238 | 0.56238 | 0.56238 | 0.56238 | 0.67486 | 0.67486 | 0.67486 | 0.67486 | 107700 | 0.0049861 | 0.0049861 | 0.0049861 | 0.0049861 | 2.4294e-12 | 2.4294e-12 | 0.12465 | 0.12465 | 0.12465 | 0.12465 | 0.14958 | 0.14958 | 0.14958 | 0.14958 | 2298500 | 0.10641 | 0.10641 | 0.10641 | 0.10641 | 5.1848e-11 | 5.1848e-11 | 2.6603 | 2.6603 | 2.6603 | 2.6603 | 3.1924 | 3.1924 | 3.1924 | 3.1924
SS-027 | c | 1D | DAPjm | 2-Way Meter - Electr | Service Switch | DAPjm shall be able to forward a service switch operate request to 2-Way Meter - Electr | SW_opr_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-003 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 206400 | 0.11944 | 0.11944 | 0.11944 | 0.11944 | 8.2758e-08 | 8.2758e-08 | 2.9861 | 2.9861 | 2.9861 | 2.9861 | 3.5833 | 3.5833 | 3.5833 | 3.5833 | 615700 | 0.35631 | 0.35631 | 0.35631 | 0.35631 | 1.9844e-08 | 1.9844e-08 | 8.9077 | 8.9077 | 8.9077 | 8.9077 | 10.6892 | 10.6892 | 10.6892 | 10.6892 | 882800 | 0.51088 | 0.51088 | 0.51088 | 0.51088 | 3.5396e-07 | 3.5396e-07 | 12.772 | 12.772 | 12.772 | 12.772 | 15.3264 | 15.3264 | 15.3264 | 15.3264 | 485900 | 0.28119 | 0.28119 | 0.28119 | 0.28119 | 4.3589e-10 | 4.3589e-10 | 7.0298 | 7.0298 | 7.0298 | 7.0298 | 8.4358 | 8.4358 | 8.4358 | 8.4358 | 107700 | 0.062326 | 0.062326 | 0.062326 | 0.062326 | 3.0368e-11 | 3.0368e-11 | 1.5582 | 1.5582 | 1.5582 | 1.5582 | 1.8698 | 1.8698 | 1.8698 | 1.8698 | 2298500 | 1.3302 | 1.3302 | 1.3302 | 1.3302 | 6.481e-10 | 6.481e-10 | 33.2538 | 33.2538 | 33.2538 | 33.2538 | 39.9045 | 39.9045 | 39.9045 | 39.9045
SS-033 | c | 1D | DAPjm | 2-Way Meter - Electr | Service Switch | DAPjm shall be able to process & forward a service switch state request to 2-Way Meter - Electr | SW_state_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-005 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 206400 | 0.11944 | 0.11944 | 0.11944 | 0.11944 | 8.2758e-08 | 8.2758e-08 | 2.9861 | 2.9861 | 2.9861 | 2.9861 | 3.5833 | 3.5833 | 3.5833 | 3.5833 | 615700 | 0.35631 | 0.35631 | 0.35631 | 0.35631 | 1.9844e-08 | 1.9844e-08 | 8.9077 | 8.9077 | 8.9077 | 8.9077 | 10.6892 | 10.6892 | 10.6892 | 10.6892 | 882800 | 0.51088 | 0.51088 | 0.51088 | 0.51088 | 3.5396e-07 | 3.5396e-07 | 12.772 | 12.772 | 12.772 | 12.772 | 15.3264 | 15.3264 | 15.3264 | 15.3264 | 485900 | 0.28119 | 0.28119 | 0.28119 | 0.28119 | 4.3589e-10 | 4.3589e-10 | 7.0298 | 7.0298 | 7.0298 | 7.0298 | 8.4358 | 8.4358 | 8.4358 | 8.4358 | 107700 | 0.062326 | 0.062326 | 0.062326 | 0.062326 | 3.0368e-11 | 3.0368e-11 | 1.5582 | 1.5582 | 1.5582 | 1.5582 | 1.8698 | 1.8698 | 1.8698 | 1.8698 | 2298500 | 1.3302 | 1.3302 | 1.3302 | 1.3302 | 6.481e-10 | 6.481e-10 | 33.2538 | 33.2538 | 33.2538 | 33.2538 | 39.9045 | 39.9045 | 39.9045 | 39.9045
SS-035 | c | 1D | 2-Way Meter - Electr | DAPjm | Service Switch | 2-Way Meter - Electr shall be able to send service switch operate acknowledgment to DAPjm | SW_opr_cmd_ack | ack | 8AM - 8PM | 1-2 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | up |  | x | SS-036 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 206400 | 0.0095556 | 0.0095556 | 0.0095556 | 0.0095556 | 6.6206e-09 | 6.6206e-09 | 0.23889 | 0.23889 | 0.23889 | 0.23889 | 0.28667 | 0.28667 | 0.28667 | 0.28667 | 615700 | 0.028505 | 0.028505 | 0.028505 | 0.028505 | 1.5875e-09 | 1.5875e-09 | 0.71262 | 0.71262 | 0.71262 | 0.71262 | 0.85514 | 0.85514 | 0.85514 | 0.85514 | 882800 | 0.04087 | 0.04087 | 0.04087 | 0.04087 | 2.8317e-08 | 2.8317e-08 | 1.0218 | 1.0218 | 1.0218 | 1.0218 | 1.2261 | 1.2261 | 1.2261 | 1.2261 | 485900 | 0.022495 | 0.022495 | 0.022495 | 0.022495 | 3.4871e-11 | 3.4871e-11 | 0.56238 | 0.56238 | 0.56238 | 0.56238 | 0.67486 | 0.67486 | 0.67486 | 0.67486 | 107700 | 0.0049861 | 0.0049861 | 0.0049861 | 0.0049861 | 2.4294e-12 | 2.4294e-12 | 0.12465 | 0.12465 | 0.12465 | 0.12465 | 0.14958 | 0.14958 | 0.14958 | 0.14958 | 2298500 | 0.10641 | 0.10641 | 0.10641 | 0.10641 | 5.1848e-11 | 5.1848e-11 | 2.6603 | 2.6603 | 2.6603 | 2.6603 | 3.1924 | 3.1924 | 3.1924 | 3.1924
SS-037 | c | 1D | 2-Way Meter - Electr | DAPjm | Service Switch | 2-Way Meter - Electr shall be able to send service switch operate faillure to DAPjm | SW_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 per 1000 per ¦ ElectrMtr per ¦ SW oper per day | > 98% | < 1 min | 50 | day |  | X | X | up |  | x | SS-038 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 60 | 60 | 50 | 1 | 2.3148e-08 | 2.3148e-08 | 206400 | 0.0047778 | 0.0047778 | 0.0047778 | 0.0047778 | 6.6206e-09 | 6.6206e-09 | 0.23889 | 0.23889 | 0.23889 | 0.23889 | 0.28667 | 0.28667 | 0.28667 | 0.28667 | 615700 | 0.014252 | 0.014252 | 0.014252 | 0.014252 | 1.5875e-09 | 1.5875e-09 | 0.71262 | 0.71262 | 0.71262 | 0.71262 | 0.85514 | 0.85514 | 0.85514 | 0.85514 | 882800 | 0.020435 | 0.020435 | 0.020435 | 0.020435 | 2.8317e-08 | 2.8317e-08 | 1.0218 | 1.0218 | 1.0218 | 1.0218 | 1.2261 | 1.2261 | 1.2261 | 1.2261 | 485900 | 0.011248 | 0.011248 | 0.011248 | 0.011248 | 3.4871e-11 | 3.4871e-11 | 0.56238 | 0.56238 | 0.56238 | 0.56238 | 0.67486 | 0.67486 | 0.67486 | 0.67486 | 107700 | 0.0024931 | 0.0024931 | 0.0024931 | 0.0024931 | 2.4294e-12 | 2.4294e-12 | 0.12465 | 0.12465 | 0.12465 | 0.12465 | 0.14958 | 0.14958 | 0.14958 | 0.14958 | 2298500 | 0.053206 | 0.053206 | 0.053206 | 0.053206 | 5.1848e-11 | 5.1848e-11 | 2.6603 | 2.6603 | 2.6603 | 2.6603 | 3.1924 | 3.1924 | 3.1924 | 3.1924
SS-039 | c | 1D | 2-Way Meter - Electr | DAPjm | Service Switch | 2-Way Meter - Electr shall be able to report & send metrology information after a successful service switch operate to DAPjm | SW_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | SS-040 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 100 | 1 | 4.6296e-08 | 4.6296e-08 | 206400 | 0.0095556 | 0.0095556 | 0.0095556 | 0.0095556 | 2.6482e-08 | 2.6482e-08 | 0.95556 | 0.95556 | 0.95556 | 0.95556 | 0.28667 | 0.28667 | 0.28667 | 0.28667 | 615700 | 0.028505 | 0.028505 | 0.028505 | 0.028505 | 6.35e-09 | 6.35e-09 | 2.8505 | 2.8505 | 2.8505 | 2.8505 | 0.85514 | 0.85514 | 0.85514 | 0.85514 | 882800 | 0.04087 | 0.04087 | 0.04087 | 0.04087 | 1.1327e-07 | 1.1327e-07 | 4.087 | 4.087 | 4.087 | 4.087 | 1.2261 | 1.2261 | 1.2261 | 1.2261 | 485900 | 0.022495 | 0.022495 | 0.022495 | 0.022495 | 1.3948e-10 | 1.3948e-10 | 2.2495 | 2.2495 | 2.2495 | 2.2495 | 0.67486 | 0.67486 | 0.67486 | 0.67486 | 107700 | 0.0049861 | 0.0049861 | 0.0049861 | 0.0049861 | 9.7177e-12 | 9.7177e-12 | 0.49861 | 0.49861 | 0.49861 | 0.49861 | 0.14958 | 0.14958 | 0.14958 | 0.14958 | 2298500 | 0.10641 | 0.10641 | 0.10641 | 0.10641 | 2.0739e-10 | 2.0739e-10 | 10.6412 | 10.6412 | 10.6412 | 10.6412 | 3.1924 | 3.1924 | 3.1924 | 3.1924
SS-041 | c | 1D | 2-Way Meter - Electr | DAPjm | Service Switch | 2-Way Meter - Electr shall be able to send service switch state data to DAPjm | SW_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 per 1000 per ¦ ElectrMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | SS-042 |  |  | 0.083333 | 1 | ElectrMtr | ElectrMtr | 30 | 30 | 100 | 1 | 5.787e-07 | 5.787e-07 | 206400 | 0.11944 | 0.11944 | 0.11944 | 0.11944 | 3.3103e-07 | 3.3103e-07 | 11.9444 | 11.9444 | 11.9444 | 11.9444 | 3.5833 | 3.5833 | 3.5833 | 3.5833 | 615700 | 0.35631 | 0.35631 | 0.35631 | 0.35631 | 7.9375e-08 | 7.9375e-08 | 35.6308 | 35.6308 | 35.6308 | 35.6308 | 10.6892 | 10.6892 | 10.6892 | 10.6892 | 882800 | 0.51088 | 0.51088 | 0.51088 | 0.51088 | 1.4159e-06 | 1.4159e-06 | 51.088 | 51.088 | 51.088 | 51.088 | 15.3264 | 15.3264 | 15.3264 | 15.3264 | 485900 | 0.28119 | 0.28119 | 0.28119 | 0.28119 | 1.7436e-09 | 1.7436e-09 | 28.1192 | 28.1192 | 28.1192 | 28.1192 | 8.4358 | 8.4358 | 8.4358 | 8.4358 | 107700 | 0.062326 | 0.062326 | 0.062326 | 0.062326 | 1.2147e-10 | 1.2147e-10 | 6.2326 | 6.2326 | 6.2326 | 6.2326 | 1.8698 | 1.8698 | 1.8698 | 1.8698 | 2298500 | 1.3302 | 1.3302 | 1.3302 | 1.3302 | 2.5924e-09 | 2.5924e-09 | 133.015 | 133.015 | 133.015 | 133.015 | 39.9045 | 39.9045 | 39.9045 | 39.9045
SS-083 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Service Switch | DAPjm shall be able to forward a scheduled cancel valve operate request to 2-Way Meter - Gas | valve_opr_cancel_cmd | cmd | 8AM - 8PM | 1-2 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-075 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 30 | 30 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 180200 | 0.0083426 | 0.0083426 | 0.0083426 | 0.0083426 | 5.7802e-09 | 5.7802e-09 | 0.20856 | 0.20856 | 0.20856 | 0.20856 | 0.25028 | 0.25028 | 0.25028 | 0.25028 | 544600 | 0.025213 | 0.025213 | 0.025213 | 0.025213 | 1.4042e-09 | 1.4042e-09 | 0.63032 | 0.63032 | 0.63032 | 0.63032 | 0.75639 | 0.75639 | 0.75639 | 0.75639 | 710300 | 0.032884 | 0.032884 | 0.032884 | 0.032884 | 2.2784e-08 | 2.2784e-08 | 0.82211 | 0.82211 | 0.82211 | 0.82211 | 0.98653 | 0.98653 | 0.98653 | 0.98653 | 275800 | 0.012769 | 0.012769 | 0.012769 | 0.012769 | 1.9793e-11 | 1.9793e-11 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.38306 | 0.38306 | 0.38306 | 0.38306 | 50900 | 0.0023565 | 0.0023565 | 0.0023565 | 0.0023565 | 1.1482e-12 | 1.1482e-12 | 0.058912 | 0.058912 | 0.058912 | 0.058912 | 0.070694 | 0.070694 | 0.070694 | 0.070694 | 1761800 | 0.081565 | 0.081565 | 0.081565 | 0.081565 | 3.9741e-11 | 3.9741e-11 | 2.0391 | 2.0391 | 2.0391 | 2.0391 | 2.4469 | 2.4469 | 2.4469 | 2.4469
SS-092 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Service Switch | DAPjm shall be able to forward a valve operate request to 2-Way Meter - Gas | valve_opr_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-084 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 180200 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 7.2252e-08 | 7.2252e-08 | 2.6071 | 2.6071 | 2.6071 | 2.6071 | 3.1285 | 3.1285 | 3.1285 | 3.1285 | 544600 | 0.31516 | 0.31516 | 0.31516 | 0.31516 | 1.7552e-08 | 1.7552e-08 | 7.8791 | 7.8791 | 7.8791 | 7.8791 | 9.4549 | 9.4549 | 9.4549 | 9.4549 | 710300 | 0.41105 | 0.41105 | 0.41105 | 0.41105 | 2.848e-07 | 2.848e-07 | 10.2763 | 10.2763 | 10.2763 | 10.2763 | 12.3316 | 12.3316 | 12.3316 | 12.3316 | 275800 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 2.4741e-10 | 2.4741e-10 | 3.9902 | 3.9902 | 3.9902 | 3.9902 | 4.7882 | 4.7882 | 4.7882 | 4.7882 | 50900 | 0.029456 | 0.029456 | 0.029456 | 0.029456 | 1.4352e-11 | 1.4352e-11 | 0.7364 | 0.7364 | 0.7364 | 0.7364 | 0.88368 | 0.88368 | 0.88368 | 0.88368 | 1761800 | 1.0196 | 1.0196 | 1.0196 | 1.0196 | 4.9677e-10 | 4.9677e-10 | 25.489 | 25.489 | 25.489 | 25.489 | 30.5868 | 30.5868 | 30.5868 | 30.5868
SS-101 | c | 1Dg | DAPjm | 2-Way Meter - Gas | Service Switch | DAPjm shall be able to process & forward a value state request to 2-Way Meter - Gas | valve_state_cmd | cmd | 8AM - 8PM | 1-50 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 30 sec | 25 | day |  | X | X | down |  | x | SS-093 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 30 | 30 | 25 | 1 | 5.787e-07 | 5.787e-07 | 180200 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 7.2252e-08 | 7.2252e-08 | 2.6071 | 2.6071 | 2.6071 | 2.6071 | 3.1285 | 3.1285 | 3.1285 | 3.1285 | 544600 | 0.31516 | 0.31516 | 0.31516 | 0.31516 | 1.7552e-08 | 1.7552e-08 | 7.8791 | 7.8791 | 7.8791 | 7.8791 | 9.4549 | 9.4549 | 9.4549 | 9.4549 | 710300 | 0.41105 | 0.41105 | 0.41105 | 0.41105 | 2.848e-07 | 2.848e-07 | 10.2763 | 10.2763 | 10.2763 | 10.2763 | 12.3316 | 12.3316 | 12.3316 | 12.3316 | 275800 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 2.4741e-10 | 2.4741e-10 | 3.9902 | 3.9902 | 3.9902 | 3.9902 | 4.7882 | 4.7882 | 4.7882 | 4.7882 | 50900 | 0.029456 | 0.029456 | 0.029456 | 0.029456 | 1.4352e-11 | 1.4352e-11 | 0.7364 | 0.7364 | 0.7364 | 0.7364 | 0.88368 | 0.88368 | 0.88368 | 0.88368 | 1761800 | 1.0196 | 1.0196 | 1.0196 | 1.0196 | 4.9677e-10 | 4.9677e-10 | 25.489 | 25.489 | 25.489 | 25.489 | 30.5868 | 30.5868 | 30.5868 | 30.5868
SS-112 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Service Switch | 2-Way Meter - Gas shall be able to send valve state data to DAPjm | valve_state_cmd_resp-data | resp-data | 8AM - 8PM | 1-50 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 5 sec | 100 | day |  | X | X | up |  | x | SS-111 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 5 | 5 | 100 | 1 | 5.787e-07 | 5.787e-07 | 180200 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 2.8901e-07 | 2.8901e-07 | 10.4282 | 10.4282 | 10.4282 | 10.4282 | 0.52141 | 0.52141 | 0.52141 | 0.52141 | 544600 | 0.31516 | 0.31516 | 0.31516 | 0.31516 | 7.0209e-08 | 7.0209e-08 | 31.5162 | 31.5162 | 31.5162 | 31.5162 | 1.5758 | 1.5758 | 1.5758 | 1.5758 | 710300 | 0.41105 | 0.41105 | 0.41105 | 0.41105 | 1.1392e-06 | 1.1392e-06 | 41.1053 | 41.1053 | 41.1053 | 41.1053 | 2.0553 | 2.0553 | 2.0553 | 2.0553 | 275800 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 9.8966e-10 | 9.8966e-10 | 15.9606 | 15.9606 | 15.9606 | 15.9606 | 0.79803 | 0.79803 | 0.79803 | 0.79803 | 50900 | 0.029456 | 0.029456 | 0.029456 | 0.029456 | 5.7408e-11 | 5.7408e-11 | 2.9456 | 2.9456 | 2.9456 | 2.9456 | 0.14728 | 0.14728 | 0.14728 | 0.14728 | 1761800 | 1.0196 | 1.0196 | 1.0196 | 1.0196 | 1.9871e-09 | 1.9871e-09 | 101.956 | 101.956 | 101.956 | 101.956 | 5.0978 | 5.0978 | 5.0978 | 5.0978
SS-121 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Service Switch | 2-Way Meter - Gas shall be able to send valve operate acknowledgment to DAPjm | valve_opr_cmd_ack | ack | 8AM - 8PM | 1-2 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 1 min | 25 | day |  | X | X | up |  | x | SS-120 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 60 | 60 | 25 | 1 | 4.6296e-08 | 4.6296e-08 | 180200 | 0.0083426 | 0.0083426 | 0.0083426 | 0.0083426 | 5.7802e-09 | 5.7802e-09 | 0.20856 | 0.20856 | 0.20856 | 0.20856 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 544600 | 0.025213 | 0.025213 | 0.025213 | 0.025213 | 1.4042e-09 | 1.4042e-09 | 0.63032 | 0.63032 | 0.63032 | 0.63032 | 1.5128 | 1.5128 | 1.5128 | 1.5128 | 710300 | 0.032884 | 0.032884 | 0.032884 | 0.032884 | 2.2784e-08 | 2.2784e-08 | 0.82211 | 0.82211 | 0.82211 | 0.82211 | 1.9731 | 1.9731 | 1.9731 | 1.9731 | 275800 | 0.012769 | 0.012769 | 0.012769 | 0.012769 | 1.9793e-11 | 1.9793e-11 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.76611 | 0.76611 | 0.76611 | 0.76611 | 50900 | 0.0023565 | 0.0023565 | 0.0023565 | 0.0023565 | 1.1482e-12 | 1.1482e-12 | 0.058912 | 0.058912 | 0.058912 | 0.058912 | 0.14139 | 0.14139 | 0.14139 | 0.14139 | 1761800 | 0.081565 | 0.081565 | 0.081565 | 0.081565 | 3.9741e-11 | 3.9741e-11 | 2.0391 | 2.0391 | 2.0391 | 2.0391 | 4.8939 | 4.8939 | 4.8939 | 4.8939
SS-130 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Service Switch | 2-Way Meter - Gas shall be able to send valve operate faillure to DAPjm | valve_opr_fail_cmd-err | cmd-err | 8AM - 8PM | 1 per 1000 per ¦ GasMtr per ¦ valve close oper per day | > 98% | < 2 min | 50 | day |  | X | X | up |  | x | SS-129 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 120 | 120 | 50 | 1 | 2.3148e-08 | 2.3148e-08 | 180200 | 0.0041713 | 0.0041713 | 0.0041713 | 0.0041713 | 5.7802e-09 | 5.7802e-09 | 0.20856 | 0.20856 | 0.20856 | 0.20856 | 0.50056 | 0.50056 | 0.50056 | 0.50056 | 544600 | 0.012606 | 0.012606 | 0.012606 | 0.012606 | 1.4042e-09 | 1.4042e-09 | 0.63032 | 0.63032 | 0.63032 | 0.63032 | 1.5128 | 1.5128 | 1.5128 | 1.5128 | 710300 | 0.016442 | 0.016442 | 0.016442 | 0.016442 | 2.2784e-08 | 2.2784e-08 | 0.82211 | 0.82211 | 0.82211 | 0.82211 | 1.9731 | 1.9731 | 1.9731 | 1.9731 | 275800 | 0.0063843 | 0.0063843 | 0.0063843 | 0.0063843 | 1.9793e-11 | 1.9793e-11 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.76611 | 0.76611 | 0.76611 | 0.76611 | 50900 | 0.0011782 | 0.0011782 | 0.0011782 | 0.0011782 | 1.1482e-12 | 1.1482e-12 | 0.058912 | 0.058912 | 0.058912 | 0.058912 | 0.14139 | 0.14139 | 0.14139 | 0.14139 | 1761800 | 0.040782 | 0.040782 | 0.040782 | 0.040782 | 3.9741e-11 | 3.9741e-11 | 2.0391 | 2.0391 | 2.0391 | 2.0391 | 4.8939 | 4.8939 | 4.8939 | 4.8939
SS-139 | c | 1Dg | 2-Way Meter - Gas | DAPjm | Service Switch | 2-Way Meter - Gas shall be able to report & send metrology information after a successful valve operate to DAPjm | valve_post-oper-info_resp-data | resp-data | 8AM - 8PM | 1-2 per 1000 per ¦ GasMtr per ¦ day | > 98% | < 30 sec | 100 | day |  | X | X | up |  | x | SS-138 |  |  | 0.083333 | 1 | GasMtr | GasMtr | 30 | 30 | 100 | 1 | 4.6296e-08 | 4.6296e-08 | 180200 | 0.0083426 | 0.0083426 | 0.0083426 | 0.0083426 | 2.3121e-08 | 2.3121e-08 | 0.83426 | 0.83426 | 0.83426 | 0.83426 | 0.25028 | 0.25028 | 0.25028 | 0.25028 | 544600 | 0.025213 | 0.025213 | 0.025213 | 0.025213 | 5.6167e-09 | 5.6167e-09 | 2.5213 | 2.5213 | 2.5213 | 2.5213 | 0.75639 | 0.75639 | 0.75639 | 0.75639 | 710300 | 0.032884 | 0.032884 | 0.032884 | 0.032884 | 9.1136e-08 | 9.1136e-08 | 3.2884 | 3.2884 | 3.2884 | 3.2884 | 0.98653 | 0.98653 | 0.98653 | 0.98653 | 275800 | 0.012769 | 0.012769 | 0.012769 | 0.012769 | 7.9172e-11 | 7.9172e-11 | 1.2769 | 1.2769 | 1.2769 | 1.2769 | 0.38306 | 0.38306 | 0.38306 | 0.38306 | 50900 | 0.0023565 | 0.0023565 | 0.0023565 | 0.0023565 | 4.5927e-12 | 4.5927e-12 | 0.23565 | 0.23565 | 0.23565 | 0.23565 | 0.070694 | 0.070694 | 0.070694 | 0.070694 | 1761800 | 0.081565 | 0.081565 | 0.081565 | 0.081565 | 1.5897e-10 | 1.5897e-10 | 8.1565 | 8.1565 | 8.1565 | 8.1565 | 2.4469 | 2.4469 | 2.4469 | 2.4469
VVC-074 | c | 4DRG | DAPjm | Feeder Regulator | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator step up command to Feeder Regulator | FeederRegulator_step_up_cmd | cmd | 24x7 | 1 per ¦ fdrVR per ¦ 2 hours | > 99.5% | < 3 sec | 250 | x hour |  | X |  | down |  | x | VVC-001 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 250 | 1 | 0.00013889 | [16 empty] | 168.3346 | 0.02338 |  | 0.02338 |  | 1.3021e-08 |  | 5.845 |  | 5.845 |  | 0.070139 |  | 0.070139 |  | 461.2359 | 0.064061 |  | 0.064061 |  | 6.9444e-09 |  | 16.0151 |  | 16.0151 |  | 0.19218 |  | 0.19218 |  | 197.4792 | 0.027428 |  | 0.027428 |  | 4.2517e-10 |  | 6.8569 |  | 6.8569 |  | 0.082283 |  | 0.082283 |  | 137.437 | 0.019088 |  | 0.019088 |  | 9.3006e-11 |  | 4.7721 |  | 4.7721 |  | 0.057265 |  | 0.057265 |  | 964.4867 | 0.13396 |  | 0.13396 |  | 6.5268e-10 |  | 33.4891 |  | 33.4891 |  | 0.40187 |  | 0.40187
VVC-075 | c | 4DRG | Feeder Regulator | DAPjm | Volt/VAR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator step up command ACK to DAPjm | FeederRegulator_step_up_ack | ack | 24x7 | 1 per ¦ fdrVR per ¦ 2 hours | > 99.5% | < 3 sec | 25 | x hour |  | X |  | up |  | x | VVC-004 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 | 0.00013889 | [16 empty] | 168.3346 | 0.02338 |  | 0.02338 |  | 1.3021e-09 |  | 0.5845 |  | 0.5845 |  | 0.070139 |  | 0.070139 |  | 461.2359 | 0.064061 |  | 0.064061 |  | 6.9444e-10 |  | 1.6015 |  | 1.6015 |  | 0.19218 |  | 0.19218 |  | 197.4792 | 0.027428 |  | 0.027428 |  | 4.2517e-11 |  | 0.68569 |  | 0.68569 |  | 0.082283 |  | 0.082283 |  | 137.437 | 0.019088 |  | 0.019088 |  | 9.3006e-12 |  | 0.47721 |  | 0.47721 |  | 0.057265 |  | 0.057265 |  | 964.4867 | 0.13396 |  | 0.13396 |  | 6.5268e-11 |  | 3.3489 |  | 3.3489 |  | 0.40187 |  | 0.40187
VVC-102 | c | 4DRG | DAPjm | Feeder Regulator | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator step down command to Feeder Regulator | FeederRegulator_step_down_cmd | cmd | 24x7 | 1 per ¦ fdrVR per ¦ 2 hours | > 99.5% | < 3 sec | 250 | x hour |  | X |  | down |  | x | VVC-007 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 250 | 1 | 0.00013889 | [16 empty] | 168.3346 | 0.02338 |  | 0.02338 |  | 1.3021e-08 |  | 5.845 |  | 5.845 |  | 0.070139 |  | 0.070139 |  | 461.2359 | 0.064061 |  | 0.064061 |  | 6.9444e-09 |  | 16.0151 |  | 16.0151 |  | 0.19218 |  | 0.19218 |  | 197.4792 | 0.027428 |  | 0.027428 |  | 4.2517e-10 |  | 6.8569 |  | 6.8569 |  | 0.082283 |  | 0.082283 |  | 137.437 | 0.019088 |  | 0.019088 |  | 9.3006e-11 |  | 4.7721 |  | 4.7721 |  | 0.057265 |  | 0.057265 |  | 964.4867 | 0.13396 |  | 0.13396 |  | 6.5268e-10 |  | 33.4891 |  | 33.4891 |  | 0.40187 |  | 0.40187
VVC-103 | c | 4DRG | Feeder Regulator | DAPjm | Volt/VAR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator step down command ACK to DAPjm | FeederRegulator_step_down_ack | ack | 24x7 | 1 per ¦ fdrVR per ¦ 2 hours | > 99.5% | < 3 sec | 25 | x hour |  | X |  | up |  | x | VVC-010 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 | 0.00013889 | [16 empty] | 168.3346 | 0.02338 |  | 0.02338 |  | 1.3021e-09 |  | 0.5845 |  | 0.5845 |  | 0.070139 |  | 0.070139 |  | 461.2359 | 0.064061 |  | 0.064061 |  | 6.9444e-10 |  | 1.6015 |  | 1.6015 |  | 0.19218 |  | 0.19218 |  | 197.4792 | 0.027428 |  | 0.027428 |  | 4.2517e-11 |  | 0.68569 |  | 0.68569 |  | 0.082283 |  | 0.082283 |  | 137.437 | 0.019088 |  | 0.019088 |  | 9.3006e-12 |  | 0.47721 |  | 0.47721 |  | 0.057265 |  | 0.057265 |  | 964.4867 | 0.13396 |  | 0.13396 |  | 6.5268e-11 |  | 3.3489 |  | 3.3489 |  | 0.40187 |  | 0.40187
VVC-130 | c | 4DRG | DAPjm | Feeder Regulator | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Regulator new config to Feeder Regulator | FeederRegulator_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrVR per ¦ 12 hours | > 99.5% | < 3 sec | 500 | x hour |  | X |  | down |  | x | VVC-013 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 1.5 | 500 | 2 | 2.3148e-05 | [16 empty] | 168.3346 | 0.0038966 |  | 0.0077933 |  | 4.3403e-09 |  | 1.9483 |  | 2.0185 |  | 0.01169 |  | 0.01169 |  | 461.2359 | 0.010677 |  | 0.021354 |  | 2.3148e-09 |  | 5.3384 |  | 5.5306 |  | 0.03203 |  | 0.03203 |  | 197.4792 | 0.0045713 |  | 0.0091426 |  | 1.4172e-10 |  | 2.2856 |  | 2.3679 |  | 0.013714 |  | 0.013714 |  | 137.437 | 0.0031814 |  | 0.0063628 |  | 3.1002e-11 |  | 1.5907 |  | 1.648 |  | 0.0095442 |  | 0.0095442 |  | 964.4867 | 0.022326 |  | 0.044652 |  | 2.1756e-10 |  | 11.163 |  | 11.5649 |  | 0.066978 |  | 0.066978
VVC-131 | c | 4DRG | Feeder Regulator | DAPjm | Volt/VAR - Centralized Control | Feeder Regulator may be able to process & forward Feeder Regulator new config ACK to DAPjm | FeederRegulator_new_config_ack | ack | 24x7 | 1 per ¦ fdrVR per ¦ 12 hours | > 99.5% | < 3 sec | 25 | x hour |  | X |  | up |  | x | VVC-016 |  |  | 0.041667 | 1 | fdrVR | fdrVR | 3 | 3 | 25 | 1 | 2.3148e-05 | [16 empty] | 168.3346 | 0.0038966 |  | 0.0038966 |  | 2.1701e-10 |  | 0.097416 |  | 0.097416 |  | 0.01169 |  | 0.01169 |  | 461.2359 | 0.010677 |  | 0.010677 |  | 1.1574e-10 |  | 0.26692 |  | 0.26692 |  | 0.03203 |  | 0.03203 |  | 197.4792 | 0.0045713 |  | 0.0045713 |  | 7.0862e-12 |  | 0.11428 |  | 0.11428 |  | 0.013714 |  | 0.013714 |  | 137.437 | 0.0031814 |  | 0.0031814 |  | 1.5501e-12 |  | 0.079535 |  | 0.079535 |  | 0.0095442 |  | 0.0095442 |  | 964.4867 | 0.022326 |  | 0.022326 |  | 1.0878e-11 |  | 0.55815 |  | 0.55815 |  | 0.066978 |  | 0.066978
VVC-158 | c | 4DCB | DAPjm | Feeder Cap Bank | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank open command to Feeder Cap Bank | FeederCapBank_open_cmd | cmd | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 150 | x hour |  | X |  | down |  | x | VVC-019 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 150 | 1 | 2.3148e-05 | [16 empty] | 897.7846 | 0.020782 |  | 0.020782 |  | 6.9444e-09 |  | 3.1173 |  | 3.1173 |  | 0.062346 |  | 0.062346 |  | 2459.9246 | 0.056943 |  | 0.056943 |  | 3.7037e-09 |  | 8.5414 |  | 8.5414 |  | 0.17083 |  | 0.17083 |  | 1053.2224 | 0.02438 |  | 0.02438 |  | 2.2676e-10 |  | 3.657 |  | 3.657 |  | 0.07314 |  | 0.07314 |  | 732.9974 | 0.016968 |  | 0.016968 |  | 4.9603e-11 |  | 2.5451 |  | 2.5451 |  | 0.050903 |  | 0.050903 |  | 5143.9289 | 0.11907 |  | 0.11907 |  | 3.481e-10 |  | 17.8609 |  | 17.8609 |  | 0.35722 |  | 0.35722
VVC-159 | c | 4DCB | Feeder Cap Bank | DAPjm | Volt/VAR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank open command ACK to DAPjm | FeederCapBank_open_ack | ack | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 25 | x hour |  | X |  | up |  | x | VVC-022 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 | 2.3148e-05 | [16 empty] | 897.7846 | 0.020782 |  | 0.020782 |  | 1.1574e-09 |  | 0.51955 |  | 0.51955 |  | 0.062346 |  | 0.062346 |  | 2459.9246 | 0.056943 |  | 0.056943 |  | 6.1728e-10 |  | 1.4236 |  | 1.4236 |  | 0.17083 |  | 0.17083 |  | 1053.2224 | 0.02438 |  | 0.02438 |  | 3.7793e-11 |  | 0.6095 |  | 0.6095 |  | 0.07314 |  | 0.07314 |  | 732.9974 | 0.016968 |  | 0.016968 |  | 8.2672e-12 |  | 0.42419 |  | 0.42419 |  | 0.050903 |  | 0.050903 |  | 5143.9289 | 0.11907 |  | 0.11907 |  | 5.8016e-11 |  | 2.9768 |  | 2.9768 |  | 0.35722 |  | 0.35722
VVC-186 | c | 4DCB | DAPjm | Feeder Cap Bank | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank close command to Feeder Cap Bank | FeederCapBank_close_cmd | cmd | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 150 | x hour |  | X |  | down |  | x | VVC-025 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 150 | 1 | 2.3148e-05 | [16 empty] | 897.7846 | 0.020782 |  | 0.020782 |  | 6.9444e-09 |  | 3.1173 |  | 3.1173 |  | 0.062346 |  | 0.062346 |  | 2459.9246 | 0.056943 |  | 0.056943 |  | 3.7037e-09 |  | 8.5414 |  | 8.5414 |  | 0.17083 |  | 0.17083 |  | 1053.2224 | 0.02438 |  | 0.02438 |  | 2.2676e-10 |  | 3.657 |  | 3.657 |  | 0.07314 |  | 0.07314 |  | 732.9974 | 0.016968 |  | 0.016968 |  | 4.9603e-11 |  | 2.5451 |  | 2.5451 |  | 0.050903 |  | 0.050903 |  | 5143.9289 | 0.11907 |  | 0.11907 |  | 3.481e-10 |  | 17.8609 |  | 17.8609 |  | 0.35722 |  | 0.35722
VVC-187 | c | 4DCB | Feeder Cap Bank | DAPjm | Volt/VAR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank close command ACK to DAPjm | FeederCapBank_close_ack | ack | 24x7 | 1 per ¦ fdrCB per ¦ 12 hours | > 99.5% | < 3 sec | 25 | x hour |  | X |  | up |  | x | VVC-028 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 | 2.3148e-05 | [16 empty] | 897.7846 | 0.020782 |  | 0.020782 |  | 1.1574e-09 |  | 0.51955 |  | 0.51955 |  | 0.062346 |  | 0.062346 |  | 2459.9246 | 0.056943 |  | 0.056943 |  | 6.1728e-10 |  | 1.4236 |  | 1.4236 |  | 0.17083 |  | 0.17083 |  | 1053.2224 | 0.02438 |  | 0.02438 |  | 3.7793e-11 |  | 0.6095 |  | 0.6095 |  | 0.07314 |  | 0.07314 |  | 732.9974 | 0.016968 |  | 0.016968 |  | 8.2672e-12 |  | 0.42419 |  | 0.42419 |  | 0.050903 |  | 0.050903 |  | 5143.9289 | 0.11907 |  | 0.11907 |  | 5.8016e-11 |  | 2.9768 |  | 2.9768 |  | 0.35722 |  | 0.35722
VVC-214 | c | 4DCB | DAPjm | Feeder Cap Bank | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Cap Bank new config to Feeder Cap Bank | FeederCapBank_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrCB per ¦ week | > 99.5% | < 3 sec | 500 | week |  | X |  | down |  | x | VVC-031 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 1.5 | 500 | 2 | 1.6534e-06 | [16 empty] | 897.7846 | 0.0014844 |  | 0.0029689 |  | 1.6534e-09 |  | 0.74222 |  | 0.76894 |  | 0.0044533 |  | 0.0044533 |  | 2459.9246 | 0.0040673 |  | 0.0081347 |  | 8.8183e-10 |  | 2.0337 |  | 2.1069 |  | 0.012202 |  | 0.012202 |  | 1053.2224 | 0.0017414 |  | 0.0034829 |  | 5.399e-11 |  | 0.87072 |  | 0.90207 |  | 0.0052243 |  | 0.0052243 |  | 732.9974 | 0.001212 |  | 0.0024239 |  | 1.181e-11 |  | 0.60598 |  | 0.6278 |  | 0.0036359 |  | 0.0036359 |  | 5143.9289 | 0.0085052 |  | 0.01701 |  | 8.2881e-11 |  | 4.2526 |  | 4.4057 |  | 0.025516 |  | 0.025516
VVC-215 | c | 4DCB | Feeder Cap Bank | DAPjm | Volt/VAR - Centralized Control | Feeder Cap Bank may be able to process & forward Feeder Cap Bank new config ACK to DAPjm | FeederCapBank_new_config_ack | ack | 24x7 | 1 per ¦ fdrCB per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-034 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 897.7846 | 0.0014844 |  | 0.0014844 |  | 8.2672e-11 |  | 0.037111 |  | 0.037111 |  | 0.0044533 |  | 0.0044533 |  | 2459.9246 | 0.0040673 |  | 0.0040673 |  | 4.4092e-11 |  | 0.10168 |  | 0.10168 |  | 0.012202 |  | 0.012202 |  | 1053.2224 | 0.0017414 |  | 0.0017414 |  | 2.6995e-12 |  | 0.043536 |  | 0.043536 |  | 0.0052243 |  | 0.0052243 |  | 732.9974 | 0.001212 |  | 0.001212 |  | 5.9051e-13 |  | 0.030299 |  | 0.030299 |  | 0.0036359 |  | 0.0036359 |  | 5143.9289 | 0.0085052 |  | 0.0085052 |  | 4.144e-12 |  | 0.21263 |  | 0.21263 |  | 0.025516 |  | 0.025516
VVC-242 | c | 4DS | DAPjm | Feeder Sensor | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Sensor new config to Feeder Sensor | FeederSensor_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 500 | week |  | X |  | down |  | x | VVC-037 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 1.5 | 500 | 2 | 1.6534e-06 | [16 empty] | 1122.2307 | 0.0018555 |  | 0.0037111 |  | 2.0668e-09 |  | 0.92777 |  | 0.96117 |  | 0.0055666 |  | 0.0055666 |  | 3074.9057 | 0.0050842 |  | 0.010168 |  | 1.1023e-09 |  | 2.5421 |  | 2.6336 |  | 0.015253 |  | 0.015253 |  | 1316.5279 | 0.0021768 |  | 0.0043536 |  | 6.7487e-11 |  | 1.0884 |  | 1.1276 |  | 0.0065304 |  | 0.0065304 |  | 916.2467 | 0.001515 |  | 0.0030299 |  | 1.4763e-11 |  | 0.75748 |  | 0.78475 |  | 0.0045449 |  | 0.0045449 |  | 6429.9111 | 0.010631 |  | 0.021263 |  | 1.036e-10 |  | 5.3157 |  | 5.5071 |  | 0.031894 |  | 0.031894
VVC-243 | c | 4DS | Feeder Sensor | DAPjm | Volt/VAR - Centralized Control | Feeder Sensor may be able to process & forward Feeder Sensor new config ACK to DAPjm | FeederSensor_new_config_ack | ack | 24x7 | 1 per ¦ fdrFS per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-040 |  |  | 0.041667 | 1 | fdrFS | fdrFS | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 1122.2307 | 0.0018555 |  | 0.0018555 |  | 1.0334e-10 |  | 0.046389 |  | 0.046389 |  | 0.0055666 |  | 0.0055666 |  | 3074.9057 | 0.0050842 |  | 0.0050842 |  | 5.5115e-11 |  | 0.1271 |  | 0.1271 |  | 0.015253 |  | 0.015253 |  | 1316.5279 | 0.0021768 |  | 0.0021768 |  | 3.3744e-12 |  | 0.05442 |  | 0.05442 |  | 0.0065304 |  | 0.0065304 |  | 916.2467 | 0.001515 |  | 0.001515 |  | 7.3814e-13 |  | 0.037874 |  | 0.037874 |  | 0.0045449 |  | 0.0045449 |  | 6429.9111 | 0.010631 |  | 0.010631 |  | 5.18e-12 |  | 0.26579 |  | 0.26579 |  | 0.031894 |  | 0.031894
VVC-270 | c | 4DRC | DAPjm | Feeder Recloser | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Recloser new config to Feeder Recloser | FeederRecloser_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrRC per ¦ week | > 99.5% | < 3 sec | 500 | week |  | X |  | down |  | x | VVC-043 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 3 | 1.5 | 500 | 2 | 1.6534e-06 | [16 empty] | 673.3384 | 0.0011133 |  | 0.0022266 |  | 1.2401e-09 |  | 0.55666 |  | 0.5767 |  | 0.00334 |  | 0.00334 |  | 1844.9434 | 0.0030505 |  | 0.006101 |  | 6.6138e-10 |  | 1.5253 |  | 1.5802 |  | 0.0091515 |  | 0.0091515 |  | 789.9168 | 0.0013061 |  | 0.0026122 |  | 4.0492e-11 |  | 0.65304 |  | 0.67655 |  | 0.0039182 |  | 0.0039182 |  | 549.748 | 0.00090897 |  | 0.0018179 |  | 8.8577e-12 |  | 0.45449 |  | 0.47085 |  | 0.0027269 |  | 0.0027269 |  | 3857.9467 | 0.0063789 |  | 0.012758 |  | 6.216e-11 |  | 3.1894 |  | 3.3043 |  | 0.019137 |  | 0.019137
VVC-271 | c | 4DRC | Feeder Recloser | DAPjm | Volt/VAR - Centralized Control | Feeder Recloser may be able to process & forward Feeder Recloser new config ACK to DAPjm | FeederRecloser_new_config_ack | ack | 24x7 | 1 per ¦ fdrCB per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-046 |  |  | 0.041667 | 1 | fdrCB | fdrCB | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 897.7846 | 0.0014844 |  | 0.0014844 |  | 8.2672e-11 |  | 0.037111 |  | 0.037111 |  | 0.0044533 |  | 0.0044533 |  | 2459.9246 | 0.0040673 |  | 0.0040673 |  | 4.4092e-11 |  | 0.10168 |  | 0.10168 |  | 0.012202 |  | 0.012202 |  | 1053.2224 | 0.0017414 |  | 0.0017414 |  | 2.6995e-12 |  | 0.043536 |  | 0.043536 |  | 0.0052243 |  | 0.0052243 |  | 732.9974 | 0.001212 |  | 0.001212 |  | 5.9051e-13 |  | 0.030299 |  | 0.030299 |  | 0.0036359 |  | 0.0036359 |  | 5143.9289 | 0.0085052 |  | 0.0085052 |  | 4.144e-12 |  | 0.21263 |  | 0.21263 |  | 0.025516 |  | 0.025516
VVC-298 | c | 4DSW | DAPjm | Feeder Switch | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Switch open command to Feeder Switch | FeederSwitch_open_cmd | cmd | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 150 | week |  | X |  | down |  | x | VVC-049 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 150 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 2.4802e-10 |  | 0.11133 |  | 0.11133 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 1.3228e-10 |  | 0.30505 |  | 0.30505 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 8.0985e-12 |  | 0.13061 |  | 0.13061 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 1.7715e-12 |  | 0.090897 |  | 0.090897 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 1.2432e-11 |  | 0.63789 |  | 0.63789 |  | 0.012758 |  | 0.012758
VVC-299 | c | 4DSW | Feeder Switch | DAPjm | Volt/VAR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch open command ACK to DAPjm | FeederSwitch_open_ack | ack | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-052 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 4.1336e-11 |  | 0.018555 |  | 0.018555 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 2.2046e-11 |  | 0.050842 |  | 0.050842 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 1.3497e-12 |  | 0.021768 |  | 0.021768 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 2.9526e-13 |  | 0.01515 |  | 0.01515 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 2.072e-12 |  | 0.10631 |  | 0.10631 |  | 0.012758 |  | 0.012758
VVC-326 | c | 4DSW | DAPjm | Feeder Switch | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Switch close command to Feeder Switch | FeederSwitch_close_cmd | cmd | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 150 | week |  | X |  | down |  | x | VVC-055 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 150 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 2.4802e-10 |  | 0.11133 |  | 0.11133 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 1.3228e-10 |  | 0.30505 |  | 0.30505 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 8.0985e-12 |  | 0.13061 |  | 0.13061 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 1.7715e-12 |  | 0.090897 |  | 0.090897 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 1.2432e-11 |  | 0.63789 |  | 0.63789 |  | 0.012758 |  | 0.012758
VVC-327 | c | 4DSW | Feeder Switch | DAPjm | Volt/VAR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch close command ACK to DAPjm | FeederSwitch_close_ack | ack | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-058 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 4.1336e-11 |  | 0.018555 |  | 0.018555 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 2.2046e-11 |  | 0.050842 |  | 0.050842 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 1.3497e-12 |  | 0.021768 |  | 0.021768 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 2.9526e-13 |  | 0.01515 |  | 0.01515 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 2.072e-12 |  | 0.10631 |  | 0.10631 |  | 0.012758 |  | 0.012758
VVC-344 | c | 4DSW | Feeder Switch | DAPjm | Volt/VAR - Centralized Control | Feeder Switch may be able to process & forward Feeder Switch new config ACK to DAPjm | FeederSwitch_new_config_ack | ack | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 25 | week |  | X |  | up |  | x | VVC-341 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 3 | 25 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 4.1336e-11 |  | 0.018555 |  | 0.018555 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 2.2046e-11 |  | 0.050842 |  | 0.050842 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 1.3497e-12 |  | 0.021768 |  | 0.021768 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 2.9526e-13 |  | 0.01515 |  | 0.01515 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 2.072e-12 |  | 0.10631 |  | 0.10631 |  | 0.012758 |  | 0.012758
VVC-374 | c | 4DSW | DAPjm | Feeder Switch | Volt/VAR - Centralized Control | DAPjm may be able to process & forward Feeder Switch new config to Feeder Switch | FeederSwitch_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrSW per ¦ week | > 99.5% | < 3 sec | 500 | week |  | X |  | down |  | x | VVC-358 |  |  | 0.041667 | 1 | fdrSW | fdrSW | 3 | 1.5 | 500 | 2 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.0014844 |  | 8.2672e-10 |  | 0.37111 |  | 0.38447 |  | 0.0022266 |  | 0.0022266 |  | 1229.9623 | 0.0020337 |  | 0.0040673 |  | 4.4092e-10 |  | 1.0168 |  | 1.0534 |  | 0.006101 |  | 0.006101 |  | 526.6112 | 0.00087072 |  | 0.0017414 |  | 2.6995e-11 |  | 0.43536 |  | 0.45103 |  | 0.0026122 |  | 0.0026122 |  | 366.4987 | 0.00060598 |  | 0.001212 |  | 5.9051e-12 |  | 0.30299 |  | 0.3139 |  | 0.0018179 |  | 0.0018179 |  | 2571.9644 | 0.0042526 |  | 0.0085052 |  | 4.144e-11 |  | 2.1263 |  | 2.2028 |  | 0.012758 |  | 0.012758
VVC-x1 | c | 4FRC | FAN gateway - field | Feeder Recloser | Volt/VAR - Centralized Control | FAN gateway - field shall be able to send Feeder Recloser new config to Feeder Recloser | FeederRecloser_new_config_cmd | cmd | 24x7 | 1 per ¦ fdrRC per ¦ week | > 99.5% | < 4 sec | 500 | week | N | X |  | down |  | x | VVC-043 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 4 | 2 | 500 | 2 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.0014844 |  | 8.2672e-10 |  | 0.37111 |  | 0.38447 |  | 0.0029689 |  | 0.0029689 |  | 1229.9623 | 0.0020337 |  | 0.0040673 |  | 4.4092e-10 |  | 1.0168 |  | 1.0534 |  | 0.0081347 |  | 0.0081347 |  | 526.6112 | 0.00087072 |  | 0.0017414 |  | 2.6995e-11 |  | 0.43536 |  | 0.45103 |  | 0.0034829 |  | 0.0034829 |  | 366.4987 | 0.00060598 |  | 0.001212 |  | 5.9051e-12 |  | 0.30299 |  | 0.3139 |  | 0.0024239 |  | 0.0024239 |  | 2571.9644 | 0.0042526 |  | 0.0085052 |  | 4.144e-11 |  | 2.1263 |  | 2.2028 |  | 0.01701 |  | 0.01701
VVC-x2 | c | 4FRC | Feeder Recloser | FAN gateway - field | Volt/VAR - Centralized Control | Feeder Recloser shall be able to send Feeder Recloser new config ACK to FAN gateway - field | FeederRecloser_new_config_ack | ack | 24x7 | 1 per ¦ fdrRC per ¦ week | > 99.5% | < 4 sec | 25 | week | N | X |  | up |  | x | VVC-046 |  |  | 0.041667 | 1 | fdrRC | fdrRC | 4 | 4 | 25 | 1 | 1.6534e-06 | [16 empty] | 448.8923 | 0.00074222 |  | 0.00074222 |  | 4.1336e-11 |  | 0.018555 |  | 0.018555 |  | 0.0029689 |  | 0.0029689 |  | 1229.9623 | 0.0020337 |  | 0.0020337 |  | 2.2046e-11 |  | 0.050842 |  | 0.050842 |  | 0.0081347 |  | 0.0081347 |  | 526.6112 | 0.00087072 |  | 0.00087072 |  | 1.3497e-12 |  | 0.021768 |  | 0.021768 |  | 0.0034829 |  | 0.0034829 |  | 366.4987 | 0.00060598 |  | 0.00060598 |  | 2.9526e-13 |  | 0.01515 |  | 0.01515 |  | 0.0024239 |  | 0.0024239 |  | 2571.9644 | 0.0042526 |  | 0.0042526 |  | 2.072e-12 |  | 0.10631 |  | 0.10631 |  | 0.01701 |  | 0.01701

## 5-SGNet-summarized-inputs
| High Density Urban |  | Urban |  | Suburban |  | Rural |  | Low Density Rural |  | Total Model Area
Model-Area | sq-mi >> | 36.0827 | sq-mi >> | 448.8923 | sq-mi >> | 2306.1793 | sq-mi >> | 16127.4674 | sq-mi >> | 51309.8159 | sq-mi >> | 70228.4375
| #endpoints >> | 512800 | #endpoints >> | 1547210.5807 | #endpoints >> | 2560871.4628 | #endpoints >> | 1044985.7574 | #endpoints >> | 186904.9278 | #endpoints >> | 5852772.7288
Metric | baseload | highload | baseload | highload | baseload | highload | baseload | highload | baseload | highload | baseload | highload
MBps/sq-mi - UpLink | 0.0012339 | 0.016129 | 0.00044858 | 0.002314 | 0.0052385 | 0.051282 | 1.0352e-05 | 6.5877e-05 | 1.4307e-06 | 2.5717e-05 | 1.7391e-05 | 0.00011946
MBps/sq-mi - DownLink | 5.1932e-06 | 0.029327 | 0.00010176 | 0.0054719 | 0.0001239 | 0.11602 | 3.292e-06 | 0.00010774 | 7.1853e-07 | 8.9903e-06 | 5.4619e-06 | 0.00019715
App Payload Rate #/s | 45.7105 | 87.7821 | 1044.995 | 1195.5622 | 3773.7568 | 4067.4504 | 1144.5642 | 1269.4819 | 756.6892 | 803.0781 | 6765.7152 | 7423.3541
App Packet Rate #/s | 208.9911 | 6403.7573 | 1535.2092 | 14193.2578 | 4447.0452 | 27748.8261 | 1466.4576 | 11522.7413 | 823.8055 | 7306.2007 | 8481.5082 | 67174.7826
App Packet Rate #/s (Uplink) | 206.9121 | 2306.784 | 1075.9407 | 4393.4698 | 2817.6675 | 9616.347 | 932.302 | 4457.1566 | 453.4019 | 5287.2247 | 5486.2238 | 26060.9821
App Packet Rate #/s (Downlink) | 2.0791 | 4096.9733 | 459.2685 | 9799.7879 | 1629.3777 | 18132.4791 | 534.1555 | 7065.5848 | 370.4036 | 2018.9759 | 2995.2843 | 41113.8005
Avg time between App payloads sec | 0.021877 | 0.011392 | 0.00095694 | 0.00083643 | 0.00026499 | 0.00024585 | 0.0008737 | 0.00078772 | 0.0013215 | 0.0012452 | 0.0001478 | 0.00013471
Avg time between App packets sec | 0.0047849 | 0.00015616 | 0.00065138 | 7.0456e-05 | 0.00022487 | 3.6038e-05 | 0.00068192 | 8.6785e-05 | 0.0012139 | 0.00013687 | 0.0001179 | 1.4887e-05
Avg time between App packets sec (Uplink) | 0.004833 | 0.0004335 | 0.00092942 | 0.00022761 | 0.0003549 | 0.00010399 | 0.0010726 | 0.00022436 | 0.0022055 | 0.00018914 | 0.00018227 | 3.8372e-05
Avg time between App packets sec (Downlink) | 0.48098 | 0.00024408 | 0.0021774 | 0.00010204 | 0.00061373 | 5.515e-05 | 0.0018721 | 0.00014153 | 0.0026998 | 0.0004953 | 0.00033386 | 2.4323e-05
weighted avg app payload (without overheads) size bytes | 978 | 18685 | 236 | 2923 | 146 | 1605 | 192 | 2206 | 146 | 2218 | 173 | 2188
weighted avg app packet (without overheads) size bytes | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 145 | 243
weighted avg app packet (without overheads) size bytes (Uplink) | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 174 | 238
weighted avg app packet (without overheads) size bytes (Downlink) | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 94 | 246
weighted avg business app payload latency sec | 5697 | 3064 | 751 | 678 | 303 | 292 | 464 | 432 | 145 | 141 | 133 | 15
weighted avg business app packet latency sec | 1246 | 42 | 511 | 57 | 257 | 43 | 362 | 48 | 133 | 15 | 334 | 44
weighted avg business app packet latency sec (Uplink) | 1256 | 114 | 727 | 179 | 404 | 119 | 567 | 120 | 238 | 21 | 513 | 109
weighted avg business app packet latency sec (Downlink) | 221 | 2 | 6 | 2 | 4 | 2 | 4 | 2 | 3 | 2 | 4 | 2
minimum business app packet latecy sec | 0.5 | 0.038845 | 0.5 | 0.5 | 0.5 | 0.038845 | 0.5 | 0.038845 | 0.5 | 0.038845 | 0.5 | 0.038845
minimum business app packet latecy sec (Uplink) | 0.5 | 0.038845 | 0.5 | 0.5 | 0.5 | 0.038845 | 0.5 | 0.038845 | 0.5 | 0.038845 | 0.5 | 0.038845
minimum business app packet latecy sec (Downlink) | 5 | 0.038845 | 1.5 | 1.5 | 1.5 | 0.038845 | 1.5 | 0.038845 | 1.5 | 0.038845 | 1.5 | 0.038845
packet size bytes (no overhead)>> | 259 |  | Fixed | << specify variable or fixed
Latency Rqmts calculation parameters (on an endpoint-packet perspective) (Uplink & Downlink)
Message Rate #/s (Rmsg) | 0.00040755 | 0.012488 | 0.00099224 | 0.0091734 | 0.0017365 | 0.010836 | 0.0014033 | 0.011027 | 0.0044076 | 0.03909 | 0.0014491 | 0.011477
Avg time between Message sec (Tmsg = 1/Rmsg) | 2453.6927 | 80.078 | 1007.8174 | 109.0103 | 575.8591 | 92.2876 | 712.5919 | 90.689 | 226.8799 | 25.5817 | 690.0627 | 87.1275
avg app packet (without overheads) size bytes (Pavg) | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 145 | 243
Single Network Link Latency sec (L) from avg bus packet latency | 996.8 | 33.6 | 408.8 | 45.6 | 205.6 | 34.4 | 289.6 | 38.4 | 106.4 | 12 | 267.2 | 35.2
Single Network Link Latency sec (L) from manual bus packet latency input | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
DAPjm to endpoint network latency rqmts sec (manual input) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
% of latency allocated to node processing | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
anticipated #network links (hops) for DAPjm to endpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Single Network Link Latency sec (L) from min bus packet latency | 0.4 | 0.031076 | 0.4 | 0.4 | 0.4 | 0.031076 | 0.4 | 0.031076 | 0.4 | 0.031076 | 0.4 | 0.031076
probability that msg event falls within latency window (Pmsg = L/Tmsg) from avg bus packet latency | 40.62% | 41.96% | 40.56% | 41.83% | 35.7% | 37.27% | 40.64% | 42.34% | 46.9% | 46.91% | 38.72% | 40.4%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from manual input of bus packet latency | 0.06521% | 1.998% | 0.1588% | 1.468% | 0.2778% | 1.734% | 0.2245% | 1.764% | 0.7052% | 6.254% | 0.2319% | 1.836%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from min bus packet latency | 0.0163% | 0.03881% | 0.03969% | 0.3669% | 0.06946% | 0.03367% | 0.05613% | 0.03427% | 0.1763% | 0.1215% | 0.05797% | 0.03567%
avg Cgp = avg PhySE x ChanBW x (1 - ChOH)
Tpkt = 8 x Pavg / Cgp
Latency Rqmts calculation parameters (on an endpoint-packet perspective) Uplink
Message Rate #/s (Rmsg) | 0.00040349 | 0.0044984 | 0.00069541 | 0.0028396 | 0.0011003 | 0.0037551 | 0.00089217 | 0.0042653 | 0.0024258 | 0.028288 | 0.00093737 | 0.0044528
Avg time between Message sec (Tmsg = 1/Rmsg) | 2478.3476 | 222.3008 | 1438.0072 | 352.1614 | 908.8622 | 266.304 | 1120.8661 | 234.4512 | 412.2279 | 35.3503 | 1066.8126 | 224.5799
avg app packet (without overheads) size bytes (Pavg) | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 174 | 238
Single Network Link Latency sec (L) from avg bus packet latency | 1004.8 | 91.2 | 581.6 | 143.2 | 323.2 | 95.2 | 453.6 | 96 | 190.4 | 16.8 | 410.4 | 87.2
Single Network Link Latency sec (L) from manual bus packet latency input | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
DAPjm to endpoint network latency rqmts sec (manual input) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
% of latency allocated to node processing | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
anticipated #network links (hops) for DAPjm to endpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Single Network Link Latency sec (L) from min bus packet latency | 0.4 | 0.031076 | 0.4 | 0.4 | 0.4 | 0.031076 | 0.4 | 0.031076 | 0.4 | 0.031076 | 0.4 | 0.031076
probability that msg event falls within latency window (Pmsg = L/Tmsg) from avg bus packet latency | 40.54% | 41.03% | 40.44% | 40.66% | 35.56% | 35.75% | 40.47% | 40.95% | 46.19% | 47.52% | 38.47% | 38.83%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from manual input of bus packet latency | 0.06456% | 0.7197% | 0.1113% | 0.4543% | 0.176% | 0.6008% | 0.1427% | 0.6824% | 0.3881% | 4.526% | 0.15% | 0.7124%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from min bus packet latency | 0.01614% | 0.01398% | 0.02782% | 0.1136% | 0.04401% | 0.01167% | 0.03569% | 0.01325% | 0.09703% | 0.08791% | 0.03749% | 0.01384%
avg Cgp = avg PhySE x ChanBW x (1 - ChOH)
Tpkt = 8 x Pavg / Cgp
Latency Rqmts calculation parameters (on an endpoint-packet perspective) Downlink
Message Rate #/s (Rmsg) | 4.0544e-06 | 0.0079894 | 0.00029684 | 0.0063338 | 0.00063626 | 0.0070806 | 0.00051116 | 0.0067614 | 0.0019818 | 0.010802 | 0.00051177 | 0.0070247
Avg time between Message sec (Tmsg = 1/Rmsg) | 246648.6462 | 125.1656 | 3368.8587 | 157.882 | 1571.6869 | 141.2312 | 1956.3324 | 147.898 | 504.598 | 92.5741 | 1953.9957 | 142.3554
avg app packet (without overheads) size bytes (Pavg) | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 94 | 246
Single Network Link Latency sec (L) from avg bus packet latency | 176.8 | 1.6 | 4.8 | 1.6 | 3.2 | 1.6 | 3.2 | 1.6 | 2.4 | 1.6 | 3.2 | 1.6
Single Network Link Latency sec (L) from manual bus packet latency input | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
DAPjm to endpoint network latency rqmts sec (manual input) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
% of latency allocated to node processing | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
anticipated #network links (hops) for DAPjm to endpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Single Network Link Latency sec (L) from min bus packet latency | 4 | 0.031076 | 1.2 | 1.2 | 1.2 | 0.031076 | 1.2 | 0.031076 | 1.2 | 0.031076 | 1.2 | 0.031076
probability that msg event falls within latency window (Pmsg = L/Tmsg) from avg bus packet latency | 0.07168% | 1.278% | 0.1425% | 1.013% | 0.2036% | 1.133% | 0.1636% | 1.082% | 0.4756% | 1.728% | 0.1638% | 1.124%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from manual input of bus packet latency | 0.0006487% | 1.278% | 0.04749% | 1.013% | 0.1018% | 1.133% | 0.08179% | 1.082% | 0.3171% | 1.728% | 0.08188% | 1.124%
probability that msg event falls within latency window (Pmsg = L/Tmsg) from min bus packet latency | 0.001622% | 0.02483% | 0.03562% | 0.7601% | 0.07635% | 0.022% | 0.06134% | 0.02101% | 0.2378% | 0.03357% | 0.06141% | 0.02183%
avg Cgp = avg PhySE x ChanBW x (1 - ChOH)
Tpkt = 8 x Pavg / Cgp
legend | calc from 4-SG-Net-Rqmts-filtered tab
manual inputs
packet metrics
From sheet C

## 7-RF-Model-Outputs
Extracted from RF Model Outputs - work-in-progress What output cells (e.g. E19-I19?) from the RF Model are used to determine the entries in the "8-Sum-Outputs" tab tan shaded cells e.g. especially the quanty of network gear and other characteristics noted, for each model-area density categories and "Baseline" and "Heavy Load" periods set of requirements

## 8-Sum-Outputs
Summary Output |  | Wireless Standard / representative technology / spectrum-band
|  | std(1) - tech : spectrum1 | [7 empty] | std(1) - tech - spectrumn | [6 empty] | . . . | std(n)
density area | Networks | # DAPs | # repeaters (opt) | delay | reliability | through-put | DAP backhaul Mbps | Payload volume, how-often, reliability Rqmts satisfied? | . . . | # DAPs | # repeaters (opt) | delay | reliability | through-put | DAP backhaul Mbps | Payload volume, how-often, reliability Rqmts satisfied?
Baseline Payloads
dense urban | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
urban | sub-total
AMI
FAN
HAN (opt)
suburban | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
rural | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
low density rural | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
Baseline + Special Event Payloads (Heavy Loading)
dense urban | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
urban | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
suburban | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
rura | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)
low density rura | sub-total
AMI
FAN
DA AMI/FAN
HAN (opt)

## 9-weight-avg-examples
weighted average | [6 empty] | weighted average
integer qty's | qty | item value | weight factor of qty | weight * value |  | qty*value (method used in framework) | mixed qty's | qty | item value | weight factor of qty | weight * value |  | qty*value (method used in framework)
| 5 | 25 | 0.096154 | 2.4038 |  | 125 |  | 5 | 25 | 0.096154 | 2.4038 |  | 125
| 6 | 30 | 0.11538 | 3.4615 |  | 180 |  | 6.4 | 30 | 0.12308 | 3.6923 |  | 192
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0
| 1 | 33 | 0.019231 | 0.63462 |  | 33 |  | 0.3 | 33 | 0.0057692 | 0.19038 |  | 9.9
| 3 | 40 | 0.057692 | 2.3077 |  | 120 |  | 3 | 40 | 0.057692 | 2.3077 |  | 120
| 1 | 50 | 0.019231 | 0.96154 |  | 50 |  | 0.4 | 50 | 0.0076923 | 0.38462 |  | 20
| 8 | 8 | 0.15385 | 1.2308 |  | 64 |  | 8 | 8 | 0.15385 | 1.2308 |  | 64
| 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0
| 10 | 15 | 0.19231 | 2.8846 |  | 150 |  | 10.3 | 15 | 0.19808 | 2.9712 |  | 154.5
| 2 | 2 | 0.038462 | 0.076923 |  | 4 |  | 2.4 | 2 | 0.046154 | 0.092308 |  | 4.8
| 7 | 20 | 0.13462 | 2.6923 |  | 140 |  | 7 | 20 | 0.13462 | 2.6923 |  | 140
| 9 | 17 | 0.17308 | 2.9423 |  | 153 |  | 9.2 | 17 | 0.17692 | 3.0077 |  | 156.4
sum qty | 52 |  |  | 19.5962 | << weighted value |  | sum qty | 52 |  |  | 18.9731 | << weighted value
|  |  | weighted average (method used in framework) >> |  |  | 19.5962 |  |  |  | weighted average (method used in framework) >> |  |  | 18.9731
classic average |  | item value |  |  |  |  | average |  | item value
|  | 25 |  |  |  |  | round qty's |  | 25
|  | 25 | [6 empty] | 25
|  | 25 | [6 empty] | 25
|  | 25 | [6 empty] | 25
|  | 25 | [6 empty] | 25
|  | 30 | [6 empty] | 30
|  | 30 | [6 empty] | 30
|  | 30 | [6 empty] | 30
|  | 30 | [6 empty] | 30
|  | 30 | [6 empty] | 30
|  | 30 | [6 empty] | 30
|  | 33 | [6 empty] | 40
|  | 40 | [6 empty] | 40
|  | 40 | [6 empty] | 40
|  | 40 | [6 empty] | 8
|  | 50 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 8
|  | 8 | [6 empty] | 15
|  | 8 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 15
|  | 15 | [6 empty] | 2
|  | 15 | [6 empty] | 2
|  | 2 | [6 empty] | 20
|  | 2 | [6 empty] | 20
|  | 20 | [6 empty] | 20
|  | 20 | [6 empty] | 20
|  | 20 | [6 empty] | 20
|  | 20 | [6 empty] | 20
|  | 20 | [6 empty] | 20
|  | 20 | [6 empty] | 17
|  | 20 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
|  | 17 | [6 empty] | 17
17
|  | 17 | [5 empty] | average>> | 18.72
| average>> | 19.5962

## A-Demographic Req. Summary
This Sheet provides a transistion & link between the 'Framework Tool' and the 'Modeling Engine'. It takes the demographic choices made on Sheet C and couples those with the appropriate 'Data Density' and 'Latency Requirements' from sheet 5. There are NO entries to be made on this sheet.
| From Sheet C | From Sheet 5
Density Area Category from Sheet C is | Suburban |  | Max Pkt Size is | 259
Total Land Area = | 2306.1793 | sq-mi | Pkt Size is | Fixed
Total # of End-Points = | 2560871.4628
| UL | Channel | DL | Channel
Baseload | 0.0052385 | MBps/sq-mi | 0.0001239 | MBps/sq-mi
Avg Baseload Pkt Size | 259 |  | 259
Average Baseload e2e Latency | 323.2 |  | 3.2
Minimum Baseload e2e Latency | 0.4 |  | 1.2
Highload | 0.051282 | MBps/sq-mi | 0.11602 | MBps/sq-mi
Avg Highload Pkt Size | 259 |  | 259
Average Highload e2e Latency | 95.2 |  | 1.6
Minimum Highload e2e Latency | 0.031076 |  | 0.031076
Network is to be designed to meet | Highload | traffic requirements
Following are the Entries Transferred to Sheet C | UL | Channel | DL | Channel
UL and DL Data (Goodput) Density Required = | 0.051282 | MBps/sq-mi | 0.11602 | MBps/sq-mi
Average Packet Size = | 259 |  | 259
Average Business Layer Latency = | 95.2 |  | 1.6
Minimum Business Layer Latency = | 0.031076 |  | 0.031076

## B-Wireless-Input-System Gain
DL/UL System Gain Calculation for | Example | Cells highlighted in yellow require an entry unless designated as n/a | [18 empty] | UPLINK Modulation & Coding Scheme (MCS) |  |  |  | DOWNLINK Modulation & Coding Scheme (MCS)
Many of the parameters on this sheet are not directly specified by the wireless standard. Generally they may be both technology-specific and vendor-specific. Base Station and Terminal parameters are required along with the modulation and coding scheme (MCS) with associated S/N estimates | [20 empty] | UL Modulation | Coding | ARQ/HARQ Repetitions | Req UL S/N in dB | DL Modulation | Coding | ARQ/HARQ Repetitions | Req DL S/N in dB
Note: The appropriate values on this sheet feed into Sheet C, Sheets 10, 11, & 12. Generally the UL system gain will be the limiting factor for link budget calculations. | [20 empty] | n/a |  | n/a |  | n/a |  | n/a
SystGaindB = Tx PwrdBm + Tx Antenna GaindBi + Rx Antenna GaindBi - Rcvr SensitivitydBm | [20 empty] | n/a |  | n/a |  | n/a |  | n/a
Maximum (or recommended) Packet Size? | 512 | Bytes | [18 empty] | n/a |  | n/a |  | n/a |  | n/a
Specify Duplex Method | FDD |  | FDD DL Chan BW = | 1 |  | FDD UL Chan BW = | 1 |  | n/a | [11 empty] | n/a |  | n/a |  | n/a |  | n/a
Entry n/a for FDD or HD-FDD | Yes |  | This Entry n/a for FDD | 2 |  |  |  |  | n/a | [11 empty] | QPSK | 0.5 | 6 | -4.3 | QPSK | 0.5 | 6 | -4.3
Entry n/a | 1.75 | [19 empty] | QPSK | 0.5 | 4 | -2.5 | QPSK | 0.5 | 4 | -2.5
Entry n/a | 1.75 | [6 empty] | λ = | 0.1499 | [11 empty] | QPSK | 0.5 | 2 | 0.5 | QPSK | 0.5 | 2 | 0.5
Frequency in MHz |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | [11 empty] | QPSK | 0.5 | 1 | 3.5 | QPSK | 0.5 | 1 | 3.5
BS Antenna Gain dBi |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [11 empty] | QPSK | 0.75 | 1 | 6.8 | QPSK | 0.75 | 1 | 6.8
Tx Amplifier Power per Antenna Element (watts) |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [11 empty] | 16QAM | 0.5 | 1 | 8.9 | 16QAM | 0.5 | 1 | 8.9
Number of Base Station Tx Antennas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [11 empty] | 16QAM | 0.75 | 1 | 13 | 16QAM | 0.25 | 1 | 13
Number of Base Station Rx Antennas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [11 empty] | 64QAM | 0.5 | 1 | 13.9 | 64QAM | 0.5 | 1 | 13.9
Base Station Rx Noise Figure dB |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [11 empty] | 64QAM | 0.66667 | 1 | 17.3 | 64QAM | 0.66667 | 1 | 17.3
This Entry n/a for Single Tx Antenna |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [11 empty] | 64QAM | 0.75 | 1 | 18.5 | 64QAM | 0.75 | 1 | 18.5
This Entry n/a for Single Rx Antenna |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [10 empty] | 1st Entry | 64QAM | 0.83333 | 1 | 20.3 | 64QAM | 0.83333 | 1 | 20.3
Is BS to BS Handover Supported ? |  | Yes
Terminal Type (Actor) |  | Fixed Outdoor Pole or Bldg-Mounted DAP | Fixed Indoor Self-Installed Terminal | Vehicular Installed Mobile Terminal | Feeder Line Device | Wireless-Enabled Smart Meter | Mobile Handheld Device | User Entry 'A' | User Entry 'B' |  |  | Fixed Outdoor Pole or Bldg-Mounted DAP | Fixed Indoor Self-Installed Terminal | Vehicular Installed Mobile Terminal | Feeder Line Device | Wireless-Enabled Smart Meter | Mobile Handheld Device | User Entry 'A' | User Entry 'B'
Best description of Network Type |  | Back-Haul Network | AMI FAN or NAN | AMI FAN or NAN | AMI FAN or NAN | AMI FAN or NAN | AMI FAN or NAN | MAN or WAN | AMI FAN or NAN
Terminal (SS) Antennna Gain dBi |  | 12 | 5 | 7 | 5 | 0 | 1 | 8 | 2
Tx Amplifier Power per Antenna Element (watts) |  | 5 | 0.5 | 0.2 | 2 | 0.5 | 0.2 | 2 | 1
Number of Terminal/(SS) Tx Antennnas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Number of Terminal/(SS) Rx Antennnas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Terminal (SS) Rx Noise Figure dB |  | 5 | 6 | 6 | 6 | 5 | 6 | 5 | 6
DL Chan OH Factor (Other PHY + Typically Layer 2: Data Link/MAC) |  | 29.3% | 29.3% | 29.3% | 29.3% | 29.3% | 29.3% | 29.3% | 29.3% | UL Chan OH Factor (Other PHY + Typically Layer 2: Data Link/MAC) |  | 30.9% | 30.9% | 30.9% | 30.9% | 30.9% | 30.9% | 30.9% | 30.9% |  | UPLINK Modulation & Coding Scheme (MCS) for Wireless Technology | [6 empty] | DOWNLINK Modulation & Coding Scheme (MCS) for Wireless Technology
Downlink System Gain Calc | Control Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Uplink System Gain Calc | Control Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel | Traffic Channel/ Subchannel |  | UL Mod/Coding Scheme | Mod Eff | Rep + Coding | UL SE Excl MAC OH (bps/Hz) | UL Layer 2 Spectral Efficiency (bps/Hz) | Req UL S/N |  | DL Mod/Coding Scheme | Mod Eff | Rep + Coding | DL SE Excl MAC OH (bps/Hz) | DL Layer 2 Spectral Efficiency (bps/Hz) | Req DL S/N
DL Channel/Sub-Channel BW (MHz) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | UL Channel/Sub-Channel BW (MHz) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | n/a | 0 | 0 | 0 | 0 | -4.3 |  | n/a | 0 | 0 | 0 | 0 | -4.3 | 0
[21 empty] | n/a | 0 | 0 | 0 | 0 | -4.3 |  | n/a | 0 | 0 | 0 | 0 | -4.3 | 0
Base Station Transmitter | [9 empty] | Terminal (SS) Transmitter | [10 empty] | n/a | 0 | 0 | 0 | 0 | -4.3 |  | n/a | 0 | 0 | 0 | 0 | -4.3 | 0
Tx Amplifier Power per Antenna Element (watts) |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Tx Amplifier Power per Antenna Element (watts) |  | 5 | 0.5 | 0.2 | 2 | 0.5 | 0.2 | 2 | 1 |  | n/a | 0 | 0 | 0 | 0 | -4.3 |  | n/a | 0 | 0 | 0 | 0 | -4.3 | 0
Base Station Cable Losses (if applicable) dB |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SS Cable Losses (if applicable) dB |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QPSK | 2 | 0.083333 | 0.16667 | 0.11517 | -4.3 |  | QPSK | 2 | 0.083333 | 0.16667 | 0.11783 | -4.3 | 0.11783
Number of Tx Antenna Elements |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Number of Tx Antenna Elements |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | QPSK | 2 | 0.125 | 0.25 | 0.17275 | -2.5 |  | QPSK | 2 | 0.125 | 0.25 | 0.17675 | -2.5 | 0.17675
Antenna Combining Gain (dB) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Antenna Combining Gain (dB) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QPSK | 2 | 0.25 | 0.5 | 0.3455 | 0.5 |  | QPSK | 2 | 0.25 | 0.5 | 0.3535 | 0.5 | 0.3535
Tx Antenna Gain (dBi) |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Tx Antenna Gain (dBi) |  | 12 | 5 | 7 | 5 | 0 | 1 | 8 | 2 |  | QPSK | 2 | 0.5 | 1 | 0.691 | 3.5 |  | QPSK | 2 | 0.5 | 1 | 0.707 | 3.5 | 0.707
Tx EIRP (dBm) |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | Tx EIRP (dBm) |  | 48.9897 | 31.9897 | 30.0103 | 38.0103 | 26.9897 | 24.0103 | 41.0103 | 32 |  | QPSK | 2 | 0.75 | 1.5 | 1.0365 | 6.8 |  | QPSK | 2 | 0.75 | 1.5 | 1.0605 | 6.8 | 1.0605
[10 empty] | For System Gain Sensitivity Analysis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16QAM | 4 | 0.5 | 2 | 1.382 | 8.9 |  | 16QAM | 4 | 0.5 | 2 | 1.414 | 8.9 | 1.414
[21 empty] | 16QAM | 4 | 0.75 | 3 | 2.073 | 13 |  | 16QAM | 4 | 0.25 | 1 | 0.707 | 13 | 0.707
Terminal (SS) Receiver | [9 empty] | Base Station Receiver | [10 empty] | 64QAM | 6 | 0.5 | 3 | 2.073 | 13.9 |  | 64QAM | 6 | 0.5 | 3 | 2.121 | 13.9 | 2.121
Rx Antenna Gain (dBi) |  | 12 | 5 | 7 | 5 | 0 | 1 | 8 | 2 | Rx Antenna Gain (dBi) |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 64QAM | 6 | 0.66667 | 4 | 2.764 | 17.3 |  | 64QAM | 6 | 0.66667 | 4 | 2.828 | 17.3 | 2.828
Number of Rx Antennas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Number of Rx Antennas |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 64QAM | 6 | 0.75 | 4.5 | 3.1095 | 18.5 |  | 64QAM | 6 | 0.75 | 4.5 | 3.1815 | 18.5 | 3.1815
Rx Antenna Diversity Gain (dB) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rx Antenna Diversity Gain (dB) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64QAM | 6 | 0.83333 | 5 | 3.455 | 20.3 |  | 64QAM | 6 | 0.83333 | 5 | 3.535 | 20.3 | 3.535
[23 empty] | Peak UL Channel Data Rate = | 5 | 3.455 | Mbps |  |  |  | Peak DL Channel Data Rate = | 5 | 3.535 | Mbps
Thermal Noise (dBm/Hz) |  | -174 | -174 | -174 | -174 | -174 | -174 | -174 | -174 | Thermal Noise (dBm/Hz) |  | -174 | -174 | -174 | -174 | -174 | -174 | -174 | -174 | [11 empty] | DL to UL Link Budget Advantage = | 13.0103 | dB
Rx Noise Figure (dB) |  | 5 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | Rx Noise Figure (dB) |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  |  | Required Cell Edge UL S/N = | -2.5 | dB |  |  |  |  | DL S/N at Cell Edge = | 10.5103 | dB
Thermal Noise Floor (dBm) |  | -109 | -109 | -109 | -109 | -109 | -109 | -109 | -109 | Thermal Noise Floor (dBm) |  | -109 | -109 | -109 | -109 | -109 | -109 | -109 | -109 | [11 empty] | DL Cell Edge Spectral Eff = | 1.414 | bps/Hz
Required DL Cell Edge Chan Data Rate (Mbps) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Required UL Cell Edge Chan Data Rate (Mbps) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | Thresh-hold UL Data Rate = | 0.11517 | Mbps |  |  |  |  | DL Cell Edge Data Rate = | 1.414 | Mbps
Required Cell Edge Spectral Efficiency (bps/Hz) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Required Cell Edge Spectral Efficiency (bps/Hz) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | "Avg" UL Layer 2 Data Rate = | 1.7851 | Mbps |  |  |  |  | "Avg" DL Layer 2 Data Rate = | 2.4745 | Mbps
Required DL Signal to Noise (dB) |  | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | Required UL Signal to Noise (dB) |  | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5 | -2.5
Rx Sensitivity (dBm) |  | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | Rx Sensitivity (dBm) |  | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5 | -111.5
Terminal Type (Actor) |  | Fixed Outdoor Pole or Bldg-Mounted DAP | Fixed Indoor Self-Installed Terminal | Vehicular Installed Mobile Terminal | Feeder Line Device | Wireless-Enabled Smart Meter | Mobile Handheld Device | User Entry 'A' | User Entry 'B' | Terminal Type (Actor) |  | Fixed Outdoor Pole or Bldg-Mounted DAP | Fixed Indoor Self-Installed Terminal | Vehicular Installed Mobile Terminal | Feeder Line Device | Wireless-Enabled Smart Meter | Mobile Handheld Device | User Entry 'A' | User Entry 'B'
DL System Gain (dB) |  | 175.5 | 168.5 | 170.5 | 168.5 | 163.5 | 164.5 | 171.5 | 165.5 | UL System Gain (dB) |  | 172.4897 | 155.4897 | 153.5103 | 161.5103 | 150.4897 | 147.5103 | 164.5103 | 155.5
Min SysGain (UL/DL/Control) for Range Calc |  | 172.4897 | 155.4897 | 153.5103 | 161.5103 | 150.4897 | 147.5103 | 164.5103 | 155.5
DL minus UL System Gain Differential |  | 3.0103 | 13.0103 | 16.9897 | 6.9897 | 13.0103 | 16.9897 | 6.9897 | 10
This table below is meant to be a guide to provide some insights as to how specific SG Terminal Types can impact the system gain and ultimately the Link Budget - 2 lines, 58 & 59, are provided for 2 additional types of ACTORS
Potential Smart Grid Terminal Type (SG Actor) | Typ Antenna Gain (dBi) | Typ Tx Pwr (Watts) | EIRP (dBm) | Comments
User Entry 'A' | 8 | 2 | 41.0103 | These rows are for entering terminal or end-point types not included in the existing selections
User Entry 'B' | 2 | 1 | 32
Mobile Handheld Device | -1.0 to 1.0 | 0.1 to 0.2 | 19 to 24 dBm | Antenna gain limited by size constraints, Tx power limited by battery/power consumption
Wireless-Enabled Smart Meter | -1.0 to 5.0 | 0.05 to 2.0 | 15 to 38 dBm | Antenna must be omni-directional, Power may be constrained by human safety exposure limits
Feeder Line Device | 3 to 7 | 0.45 to 2.0 | 30 to 40 dBm
Vehicular Installed Mobile Terminal | 5 to 9 | 0.2 | 28 to 32 dBm | Antenna size constraints, human safety exposure limitations
Fixed Indoor Self-Installed Terminal | 4 to 6 | 0.1 to 0.2 | 24 to 29 dBm | Antenna size constraints, human safety exposure limitations
Fixed Outdoor Pole or Bldg-Mounted DAP | 10 to 17 | 2 to 10 | 43 to 57 dBm | Antenna gain will generally be higher in the higher frequency bands. EIRP regulatory limits may differ in different frequency bands
Wireless ATs for FAN, NAN, MAN, WAN, or Back-Haul | Example | GSM/EDGE | WCDMA | HSPA+ | CDMA 2000 | HRPD/EV-DO | xHRPD | LTE | WiMAX-802.16e | WiMAX-802.16n,m,p | WiFi-802.11 | AT-1 | AT-2 | AT-3
Notes:
A) Terminal antenna gains and Tx pwr will vary with "Actor" type- i.e. a mobile handset will have a low gain antenna and low Tx pwr, a DAP backhaul will have a higher gain antenna with higher Tx pwr.
B) Different frequency bands may have different regulatory constraints on EIRP - unlicensed vs. licensed for example.
C) BS Transmit power may have differing maximum EIRP limits for different frequency bands.
D) It is important to know what the DL and UL OH factors include. Many responses will only account for Layers 1 and 2 (PHY and Data Link). There is provision on Sheet C to add to the OH factor to account for OH with the higher layers.
Decreasing Mod Efficiency (up to 15 entries)
For possible future use. Can list key parameters with applicable values and have these selected by choice made in cell B2. AT-1, AT-2, AT-3 are for any other Access Technology.

## C-SG Ntwrk-Input-BS-Output
Smart Grid Input Data & Coverage Requirements |  |  | Relevant Land Area (Frmwrk #5)11 = | 2306.1793 | sq-mi
Input or select entries for cells highlighted in yellow |  |  | Total number End-Points in Area (Frmwrk #5)11 = | 2560871.4628 | + or - # of End-Points | 0%
Cell color denotes values transferred from | Sheet A Demo Req | Sheet B Wireless | Density of End-Points = | 1110.439 | End-Points/sq-mi
Demographic Area to Analyzed? | Suburban |  | 100 to 999 HU/sq-mi | 111044 | = Number of End-Points in Area of Interest
Land Area of region to be covered = | 100 | sq-mi | Select Terrain Type for this demographic area | Type C | Flat with light tree density
End-Point or terminal type that best fits Smart Grid "Use Case" being analyzed (If multiple types, best to choose "worse case", i.e. the terminal with lowest system gain) | Wireless-Enabled Smart Meter | 13.0103 | Input parameters, in some cases, will be within a range that is valid for 2 or more PL models. In some of these cases, results may differ significantly. It is up to the user to decide which result to use for initial planning purposes. In all cases it is important to remember that this type of analysis should always be supplemented with more detailed site-specific RF planning prior to deployment.
Based on End-Point or Terminal choice; best description of the network type is | AMI FAN or NAN | 100 | This entry n/a for AMI, FAN, or NAN
Spectrum is "Dedicated" or "Shared" | Dedicated |  | The following rows show some of the interim calculations for each of the valid PL models leading to a final result
Is BS to BS Handover Supported? | Yes
For 'Handover', select total number of paths | 3
Duplexing Method is | FDD |  | k=4 is recommended, 0 sets Erceg back to original form10 | 4
Operating Frequency Band = | 2000 | 0.1499 | Path Loss Model | Erceg-SUI-Modified | Hata-Okumura | Cost231-Hata | WINNER II | ITU-R M.2135-14
Required Cell Edge UL Channel Goodput = | 0.25 | 2.764 | Deployment Region | Type C | Suburban | Suburban | Suburban | n/a | Units
Required Cell Edge DL Channel Goodput = | 0.25 | 2.828 | Link Budget = | 156.416 | 156.416 | 156.416 | 156.416
Resulting DL Cell Edge SNR = | 13.3103 |  | Range projection = | 2.5378 | n/a | n/a | n/a | n/a | km
(Lowest of DL/UL/Control) System Gain = | 163.5 |  | Cell Coverage Area at Maximum Range1 = | 16.7329 |  |  |  |  | sq-km
Effective DL Channel BW = | 1 |  | Cell SE Density at Maximum Range2 = | 0.24503 | n/a | n/a | n/a | n/a | bps/Hz/sq-km
Estimated Channel OH for Encryption = | 10% |  | Avg Cell Data Density at Maximum Range = | 0.37268 |  |  |  |  | bps/Hz/sq-km
Additional, Higher Layer (3+) Channel OH = | 10% | Layer 3+ Typ | Data Goodput per Cell/BS at Maximum Range3 = | 6.2361 |  |  |  |  | Mbps
Total Channel OH = | 49.3% |  | Required Cell SE Density = | 0.23562 |  |  |  |  | bps/Hz/sq-km
Maximum Packet Payload Size (net after OH) = | 259 | Fixed | Range for Required UL Data Density = | 2.5378 |  |  |  |  | km
Frequency Re-Use Factor = | 1 |  | Coverage Area per Cell at Required BS-to-BS Spacing = | 16.7329 |  |  |  |  | sq-km
Base Station Antenna Height = | 10 |  | Data Goodput/Sector at Required BS-to-BS Spacing = | 2.0787 |  |  |  |  | Mbps/Sector
Terminal (End-Point/Actor) Antenna Height = | 2
Terminal (End-Point/Actor) Location is | Outdoor
Required Cell Edge Availability = | 96.01% | 65.83% | The following Rows provide BS deployment estimates to meet Coverage, Capacity, and Latency requirements
Size ntwrk capacity (goodput) to comply with | Highload | demand | Minimum number of BS6 for ubiqutous coverage = | 16 |  |  |  |  | BS for Capacity & Coverage
Add'l Capacity for Growth or Capacity Mgn | 0%
Capacity-Limited Traffic Direction is | DL | DL | Total # of End-Points per Sector or Channel = | 2314 |  |  |  |  | End-Points/Channel
Sys Gain Variation for Sensitivity Analysis = | 0 |  | Approximate # of End-Points per Sector or Channel based on Latency Requirement8 = | 2351 |  |  |  |  | End-Points/Channel
Required incremental7 Data (Goodput) Density for SG Network in MBps/unit area = | 0.11602 | MBps/sq-mi | Additional Base Stations Required to meet Latency Requirements = | 0 |  |  |  |  | Additional BS for Latency
Required incremental7 Data (Goodput) Density for SG Network in Mbps/unit area = | 0.92818 | Mbps/sq-mi | Total # of BS for Coverage, Capacity, & Latency = | 16 |  |  |  |  | Total Base Stations
Average Packet Size = | 259 |  | Average Coverage Area per BS = | 6.25 |  |  |  |  | sq-mi
Time between packets = 1/RMSG = TMSG = | 2.4789 |  | Average BS-to-BS Spacing5 = | 2.6864 |  |  |  |  | mi
E2E Appl Layer Latency from SG Req = | Average | 1.6 | Approximate Goodput/Base Station (Mbps) ≥ | 6.2361 |  |  |  |  | Mbps/BS
This entry n/a | 0.5 | 1.6 | Net Cell/BS Spectral Efficiency (bps/Hz) ≥ | 6.2361 |  |  |  |  | bps/Hz/cell
'Business'/ higher layer Latency Contribution = | 100 |  | Excess Area Data (Goodput) Capacity9 in % ≥ | 7.498% |  |  |  |  | Per cent
Estimated Node Processing Time (Layer 1/2) = | 50 |  | Deployment is limited by ……. | Range
E2E Number of Air Links = | 1 |  | Net # of End-Points per BS = | 6941
Latency Requirement for Single Link = | 1.4 | 56.48%
E2E Confidence Level = | 99.5% | 99.5%
Effective DL Spectrum Used = | 1 |  | Footnotes:
DL SysGain/LB minus UL SysGain/LB = | 13.0103 |  | 1. Cell coverage area assumes hexagonal shape
Ratio of UL/DL Data Density Req = | 0.442 |  | 2. Spectral efficiency in this line includes only modulation efficiency and coding rate (PHY Layer Spectral Efficiency)
UL Channel Cap/DL Channel Cap = | 0.72139 |  | 3. Actual data thruput or "goodput" based on selected channel BW, technology-specific MAC/control channel OH, plus higher level OH
Average Building and Road width information is necessary for IRU-R M.2135-1 Path Loss Model |  |  | 4. Urban Micro-Cell for ITU-R M.2135-1 model ONLY valid for 10 m BS antenna & SS antenna height between 1 m & 2.5 m; Rural Micro-Cell for ITU-R 2135 is considred valid for frequency range 450 MHz to 6000 MHz
Urban Large City Bldg Height | 30 |  | 5. BS-to-BS spacing assumes a hexangular shaped coverage area
Urban Large City Road Width | 20 |  | 6. Assumes 3-Sector base station, rounded up to next whole number
Urban Small City Bldg Height | 20 |  | 7. If the intent is to overlay or take advantage of an existing wireless network, the existing network must have at least this much excess capacity to handle SG data density requirements. For a "Greenfield" deployment, this represents the total data density required for SG.
Urban Small City Road Width | 20
Suburban Bldg Height | 8 |  | 8. This value assumes that 1/2 of Actors or Terminals are operating at a level higher than the cell-edge goodput
Suburban Road Width | 20 |  | 9. Even in Capacity-Limited deployments there may be excess capacity since the number of required base stations are rounded up to the next whole number
Rural Bldg Height | 8 |  | 10. Results at 2000 MHz are independent of k. Original Erceg (k = 4) is only valid for frequency range from 1800 MHz to 2700 MHz.
Rural Road Width | 15 |  | 11. The land area and number of 'End-Points' is one-fiftieth of total US for the selected 'Demographic' category, i.e. 'Average' US state
Notes for Informative Purposes:
Type of Smart Grid Terminal | Typical Terminal Antenna Heights |  | Path Loss Models & Applicable Frequency Band | Deployment Region Description
Mobile Handheld Device | 1-2 | meters | Erceg-SUI-Modified | Type A | Hilly with moderate to heavy tree density
Wireless-Enabled Smart Meter | 2 | meters | 700-6000 MHz | Type B | Hilly with light tree density or flat with medium to heavy tree density
Feeder Line Device | 8-10 | meters |  | Type C | Flat with light tree density
Vehicular Installed Mobile Terminal | 2-3 | meters | Hata-Okumura | Large City Urban |  | BS antenna must be higher than rooftop (>30 m)
Fixed Indoor Self-Installed Terminal | 1-2 | meters | 200-1500 MHz | Small City Urban |  | "
Fixed Outdoor Pole or Bldg-Mounted DAP | 8-10 | meters |  | Suburban |  | "
User Entry 'A' |  |  | COST231-Hata | Large City Urban |  | BS antenna must be higher than rooftop (>30 m)
User Entry 'B' |  |  | 1500-2000 MHz | Suburban |  | "
Relationships and Relevant Conversion factors |  |  | WINNER II | Large City Urban |  | BS antenna must be higher than rooftop (>25 m)
1 km = | 0.62137 | mi | 2000-6000 MHz | Suburban |  | "
1 mi = | 1.6093 | km |  | Rural Open |  | "
1 sq-mi = | 2.59 | sq-km | ITU-R M.2135-1 | Large City Urban |  | Requires entry for average bldg height & road width
1 Acre = | 0.0040469 | sq-km | 2000-6000 MHz | Small City Urban |  | "
Over-the-air Propagation time = | 3.3356 | μsec/km |  | Suburban |  | "
Peak UL Channel Data Rate = | 3.455 | Mbps |  | Urban Micro-Cell |  | Manhattan-like building grid
Peak DL Channel Data Rate = | 3.535 | Mbps | 450-6000 MHz | Rural |  | Requires entry for average bldg height & road width
Minimum UL Cell Edge Rate = | 0
Maximum UL Data Rate = | 2.764
Minimum DL Cell Edge Rate = | 0
Maximum DL Data Rate = | 2.828
For Fade Margin Calculation | Avail @ D | Fm/σ =
| 50% | 0
| 65.01% | 0.3855
| 75% | 0.6745
| 80.02% | 0.8425
| 85.01% | 1.037
| 87.01% | 1.127
| 90.01% | 1.282
| 93% | 1.476
| 96.01% | 1.752
| 99.01% | 2.33

## 0-Revision History
Revision | Date | Description | Revised by
v1.4 | 2011-08-06 | Worksheet #1: Added SG application table | dg
|  | Worksheet #3: Completed calculations for WINNER II & COST231 models | dg
|  | Worksheet #3: Changed data vs SnR table to cover only modulation efficiency and code rate - eliminates MAC OH & makes it more generic rather than technology-specific | dg
v1.5 | 2011-08-11 | Worksheet #2: Corrected an error in ITU-R M.2135-1 calculation | dg
|  | Worksheet #2: Added capability to enter alternative values for k for Mod Erceg-SUI model | dg
v1.6 | 2011-08-15 | Added usage warnings | dg
v1.7 | 2011-08-16 | Worksheet #3: Added capabilty to estimate cell capacity at a specified BS-to-BS spacing | dg
|  | Added Worksheet 3a to calculate channel and cell spectral effiency rather than data rate - for data thruput SE value would have to be multiplied by (1-OH) & Channel BW | dg
v1.8 | 2011-08-18 | Worksheet #1: Added columns for varied SG applications and system gains | dg
|  | Added Sheet 1a for data density calculations also consolidated input data to two sheets, 1 and 1a (except for inter-operator interference) | dg
|  | Found and fixed several bugs | dg
|  | Worksheet 2: Added ITU-R M.2135 Urban Micro-Cell PL Model for range calculation | dg
|  | Added range calculation for ITU-R M.2135 Urban Micro-Cell Model for Manhattan-type grid layout - supports 10 m antenna heights for urban micro-cell | dg
|  | Added expanatory notes on Sheet 1a | dg
v1.9 | 2011-08-23 | Converted to a hexagonal cell shape & corrected area calculation & some other errors on sheet 1a | dg
|  | Added provision on sheet 1a to enter BS-to-BS spacing individually for each path loss model | dg
|  | Added some additional useful metrics, such as net spectral efficiency and UL spectrum requirements, also added some footnotes on sheet 1a to clarify output data | dg
v2.0 | 2011-08-28 | Modified sheet 1a to enable entry for "Required UL Data Density" and provide output indicating the necessary BS-to-BS spacing to achieved the desired data density. | dg
v2.1 | 2011-08-31 | Corrected note related to ITU Urban Micro-cell SS antenna height | dg
|  | Sheet 3: Adjusted data rates to include OH factor - note: this sheet is not used for calulations on sheet 1a, but it does provide some useful plots. | dg
| 2011-09-14 | Sheet 1a-SG Input Data: Addded capability to enter required Cell-Edge Availability, range 80% to 99% | dg
| 2011-09-23 | Sheet 3a: Found and corrected a calculation error for distance dependancy calculation | dg
v2.2 | 2011-10-02 | Update nomenclature to be more consistent with SG SRS | dg
| 2011-10-03 | A number of minor edits | dg
v2.3 | 2011-10-10 | Changed terminal options to better fit terminal description for SG Use Case | dg
| 2011-10-12 | Sheet 2: Filled out penetration loss table - consistent with NISTIR Section 5 rewrite | dg
| 2011-11-08 | Completed data density calculations for ITU-R M.2135 Urban Micro-Cell Model | dg
| 2011-11-08 | Added protection to all but Sheet 1 - PW to unprotect is 123 | dg
v2.4 | 2011-11-15 | Sheet 1: Added input for "Dedicated" or "Shared" spectrum -choice impacts value for interference margin | dg
|  | Sheet 2: Added values for inter-operator interferenced based on dedicated or shared spectrum | dg
v2.5 | 2011-12-01 | Added more explanatory notes and miscellaneous edits | dg
|  | Sheet 1a: Added input (up to 15%) for any additional higher layer OH factors not accounted for in OH entry on sheet 1. | dg
v2.6 | 2011-12-12 | Sheet 1a: Changed input data density units to Megabytes/sec/area (sq-mi or sq-km) | dg
| 2012-01-16 | Sheet 1a: Added "incremental" with footnote to SG DD requirements to cover use of existing network. | dg
|  | Also added more explanatory notes | dg
v2.7 | 2012-02-15 | Changed worksheet names: Sheet 1 now Sheet B-Wireless Input System Gain, Sheet 1a now Sheet C: Input SG Ntwrk InpuBS Output - Numbered worksheets, 1 thru 3 are only for calculations and background information | dg
| 2012-02-17 | Added Work Sheet A: Model Area Demographics (Sheet from Framework file) for deriving Data density requirements | dg
| 2012-02-19 | Edited some of the explanatory notes | dg
| 2012-03-01 | Added provision for separate entry for channel encryption OH | dg
| 2012-03-01 | Began to add provision for DL vs UL variant | dg
| 2012-03-06 | Added functionality for TDD with assymetric DL/UL Traffic | dg
v2.8 | 2012-03-09 | Adjusted Cell input to Sheet B to account for higher level OH factors | dg
| 2012-03-12 | Corrected "Bug" on Sheet A in Erceg Type selection | dg
| 2012-03-12 | Developed an algorithm to determine limiting traffic direction (UL or DL) | dg
v2.9 | 2012-03-22 | Added Worksheet 4 to incorporate Latency Model | dg
| 2012-03-23 | Sheet C: Added actual actors per channel or sector and provided number of actors per channel or sector to meet latency requirements | dg
| 2012-03-23 | Sheet A: Added input entries necessary for latency analysis | dg
| 2012-03-24 | Other minor edits to improve usability | dg
v3.0 | 2012-03-29 | Added Sheet 4: Latency Model and included latency-limited terminals per sector as an output on Sheet C - Assumes average channel goodput for estimate | dg
| 2012-04-01 | Sheet C: Fixed a bug in Goodput calculation when range limited | dg
v3.1 | 2012-04-07 | Sheet 4: Fixed incorrect parameter lables | dg
| 2012-04-08 | Sheet A: Added calulation for probability calulation based on number of message events | dg
| 2012-04-09 | Misc minor edits and bug fixes | dg
v3.2 | 2012-04-10 | Added capacity/SE adjustment for DL Spatial Multiplexing and UL MU-MIMO | dg
|  | Sheet C: Added calculation for area excess capacity | dg
| 2012-04-11 | Sheet C: Added calculation for additional Base Stations needed to meet Latency Requirements and restructured output parameters to reflect the change | dg
| 2012-04-12 | Sheet A: Added provision for entering capacity requirements anticipated for future growth | dg
v3.3 | 2012-04-14 | Added calculations for DL spectral efficiency | dg
| 2012-04-18 | Sheet B: Changed approach for entering Modulation, Coding, & Req S/N to eliminate a potential error in calculating the system gain | dg
v3.4 | 2012-04-28 | Minor bug fixes and additional explanatory labeling | dg
| 2012-05-20 | Changed file name to Wireless Modeling Tool | dg
v3.5 | 2012-06-06 | Sheet A: Added provision to enter business processing % for latency | dg
|  | Sheet A & C: Moved entries for higher layer and encryption OH from sheet C to Sheet A | dg
| 2012-06-08 | Sheet 4 and Sheet C: Fixed some bugs | dg
| 2012-06-21 | Added provision to enter number of links (or hops) for Latency requirement | dg
v3.6 | 2012-07-12 | Worksheet C: Added provision to select Baseload or Highload (cell B24) | dg
| 2012-07-12 | Worksheet A: Revised format to fit with Ron's input format, calculate Events/Hr from Data Density Requirements and Avg Pkt size | dg
v3.7 | 2012-07-25 | Worksheet B: Added input for Packet Size, added more explanatory notes | dg
|  | Worksheet A: Format to comply with latency inputs from Framework tool | dg
| 2012-08-10 | Worksheet C: Added capability to support parallel propagation paths, e.g. BS handover, Mesh, self-configuring network, etc - inputs sheet C ( Cells B7,B8) transfers to Worksheet 1 | dg
| 2012-09-10 | Worksheet C: Added provision to do Sys Gain sensitivity analysis (Cell B8) | dg
v3.8 | 2012-09-12 | Revised where input parameters are entered between Sheets A and C and cut down on linkages between these 2 sheets to make it easier to merge with Ron' Framework worksheet in the future | dg
| 2012-09-28 | Provided some additional notes, error messages, etc | dg
v3.9 | 2012-10-03 | Added network option for WAN with 'Pole-Mounted Terminal', select number for estimated end-points | dg
| 2012-10-03 | Worksheet C: Accounted for OH in Packet size - this then transfers to Frmwrk tool | dg
| 2012-10-03 | Worksheet C: Added option for 'Fixed' or 'Variable' packet size | dg
| 2012-10-08 | Worksheet C: Added provision to change 'k factor' for Erceg PL model | dg
| 2012-10-08 | Worksheet B: Added provision to declare some terminal descriptions as 'n/a' | dg
v4.0 | 2012-10-12 | Minor editing for ease of use | dg
| 2012-10-20 | Worksheets B & C: Added provision for "Back-Haul Network" as default for "Pole-Mounted DAP", BS to BS handover n/a for this network choice, Changed 'WAN' to ' MAN or WAN'. Theswe network choices require entries for the number of end-points or terminals. | dg
r0.7d-v4.0 | 2012-10-27 | This version combines the 'Framework Tool' with the 'Wireless Modeling Tool'. File name revision denotes version of each, i.e. r0.7d refers to "Framework Tool', v4.0 refres to 'Wireless Modeling Tool'. | dg
r0.7e-v4.1 | 2012-10-30 | Corrected the payload latency for the broadcast and multicast payloads | rc
|  | Put in code (hidden rows at the top of tab 4), that get used in the minimum packet latency calcs in tab 5, did not require any macro work) | rc
| 2012-11-03 | Sheet C: Added some more explanatory comments. | dg
Open Items or enhancements that can be considered for future work:
1 | Sheet B: Sheet is structured to support key parameter entries for different ATs, row 69 and below. Need consensus on which parameters.
2 | Sheet 10: Additional reference data is desirable to validate penetration loss estimates relative to frequency
3 | Sheet 10: May need inputs for self & interoperator-interference margins moved to Sheet B to reflect differences between technologies?
4 | Possible improvements: Add an input parameter to account for grossly non-uniform actor distribution
5 | Possible Improvements: Add a variation for more Extreme Terrain Characteristcs by combining Foliage & Diffraction model with Free Space Loss
6 | For Indoor scenarios it would be best to construct a separate standalone tool with a similar structure.

## 10-Range_Estimator
Note: This sheet is for calculating Range, there are no entries to be made on this sheet.
10-Range Estimation Tool
Frequency = | 2000 | MHz |  | BS Antenna Height = | 10 | meters | UL Topology= | PMP | From Worksheet C
System Gain = | 163.5 | dB |  | SS Antenna Height = | 2 | meters | # of Paths = | 3 | From Worksheet C
Cell Edge SNR + 10 dB = | 23.3103 | dB |  | Terminal (SS) Location is | Outdoor
Frequency Re-Use Factor = | 1 | (for 3-sector cell) |  | Cell-Edge % = | 65.83% | Parameter for Mod Erceg-SUI
Inter-Operator Interference Mgn = | 0 |  | 0 | 0 | dB | k = | 4
Bldg Height & Road width required for ITU-R 2135-1 Path Loss Model | Urban Large City | Urban Small City | Suburban | Rural |  |  | 10
Avg Building Height (h in meters) = | 30 | 20 | 8 | 8
Avg Road Width (W in meters) = | 20 | 20 | 20 | 15
Estimated Range (D in km)
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | Applicable Freq Range
Erceg-SUI -Modified | [5 empty] | 2.2254 | 2.4034 | 2.5378 | 700-6000
Erceg-SUI-Original | [5 empty] | 2.2254 | 2.4034 | 2.5378 | 1800-2700
Hata-Okumura | n/a | n/a | n/a | [5 empty] | 200-1500
COST231-Hata | n/a |  | n/a | [5 empty] | 1500-2000
WINNER II | n/a |  | n/a |  | n/a |  |  |  | 2000-6000
ITU-R M.2135-1 | n/a | n/a | 2.3374 | 2.2219 |  |  |  |  | 2000-6000
ITU-R M.2135-1 Urban Micro-Cell | 2.8264 | [7 empty] | 2000-6000
Path Loss Exponent (n) as in 10nLog(d/do) | [6 empty] | 1. Valid from 450 to 6000 for Rural
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | Applicable Freq Range
Erceg-SUI -Modified | [5 empty] | 5.785 | 5.645 | 5.55 | 700-6000
Erceg-SUI-Original | [5 empty] | 5.785 | 5.645 | 5.55 | 1800-2700
Hata-Okumura | n/a | n/a | n/a | [5 empty] | 200-1500
COST231-Hata | n/a |  | n/a | [5 empty] | 1500-2000
WINNER II | n/a |  | n/a |  | n/a |  |  |  | 2000-6000
ITU-R M.2135-1 | n/a | n/a | 4.032 | 4.032 |  |  |  |  | 2000-6000
ITU-R M.2135-1 Urban Micro-Cell | 3.67 | [7 empty] | 2000-6000
Excess Loss frequency dependancy (dB per Octave)
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | Applicable Freq Range
Erceg-SUI -Modified | [5 empty] | 5.109 | 4.6755 | 4.3865 | 700-6000
Erceg-SUI-Original | [5 empty] | 1.7856 | 1.7856 | 1.7856 | 1800-2700
Hata-Okumura | n/a | n/a | n/a | [5 empty] | 200-1500
COST231-Hata | n/a |  | n/a | [5 empty] | 1500-2000
WINNER II | n/a |  | n/a |  | n/a |  |  |  | 2000-6000
ITU-R M.2135-1 | n/a | n/a | 0 | 0 |  |  |  |  | 2000-6000
ITU-R M.2135-1 Urban Micro-Cell | 1.8062 | [7 empty] | 2000-6000
Lookup Table for Applicable Link Margins in dB (Need SDO group consensus on applicable numbers)
Margin | Urban Large City | Urban Small City | Suburban | Rural | Rural Open | Type A | Type B | Type C |  | Fm at D | σ = | Avail @ D | Fm/σ =
Typical Std Dev (σ) for PL Model | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | 1 | 50% | 0
Log-Normal Fade Margin = | 2.313 | 2.313 | 3.084 | 3.084 | 3.084 | 3.084 | 3.084 | 3.084 |  | 0.3855 | 1 | 65.01% | 0.3855
Fast Fade Margin = | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 0.6745 | 1 | 75% | 0.6745
Self-Interference Margin = | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 0.8425 | 1 | 80.02% | 0.8425
Inter-0perator Interference Margin = | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.037 | 1 | 85.01% | 1.037
Allowance for Penetration Loss = | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.127 | 1 | 87.01% | 1.127
Total Margin = | 6.313 | 6.313 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 |  | 1.282 | 1 | 90.01% | 1.282
Lookup Table for Penetration Loss in dB (Values in bold italics taken from reference material) | [9 empty] | 1.476 | 1 | 93% | 1.476
Frequency | Outdoor | Vehicle | Indoor-Res | Indoor-Bus | Indoor-Basement | Indoor-Vault |  |  |  | 1.752 | 1 | 96.01% | 1.752
700 | 0 | 9 | 7.5 | 10 | 17 | 27 |  |  |  | 2.33 | 1 | 99.01% | 2.33
1000 | 0 | 9 | 7.7 | 13 | 18 | 28 | These numbers based on NTIA document
2000 | 0 | 9 | 11.6 | 20 | 24 | 30 | Inside Vehicle based on ITU-R M.2135 Recommendation
3000 | 0 | 9 | 13 | 24 | 28 | 32
4000 | 0 | 9 | 14 | 27 | 30 | 34
5000 | 0 | 9 | 15 | 29 | 31 | 35
6000 | 0 | 9 | 16.2 | 31 | 31.5 | 36
Additional Margin (std dev) = | 0 | 5 | 5 | 6 | 6 | 8
Erceg-SUI Model Modified |  |  | Valid from 700 MHz to 6000 MHz
L = 20*LOG(4p d0 /l)+10*(a-b*hb+c/hb)*LOG(d/ d0) + 6(1+ak/hb)LOG(f/2000) - XLOG(hr/2)
LOG(d/d0) = [LB - 20*LOG(4π d0 /λ) - 6(1+ak/hb)LOG(f/2000)+XLOG(hr/2)]/[10*(a-b*hb+c/hb)]
d = d0 10LOG(d/d0)
|  |  | k= | 4 | Type A |  | Type B |  | Type C
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 11.1296 | dB/Octave = | 10.6961 | dB/Octave = | 10.4071
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 57.85 | dB/decade = | 56.45 | dB/decade = | 55.5
| BS Antenna (hb in m)= | 10 | d0= | 100 | a= | 4.6 | a= | 4 | a= | 3.6
| SS Antenna (hr in m)= | 2 |  |  | X= | 10.8 | X= | 10.8 | X= | 20
|  |  | System Gain | Loss at do | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 | 78.4685 | 156.416 | 2.2254 | 156.416 | 2.4034 | 156.416 | 2.5378
Erceg-SUI Model Original |  |  | Valid from 1800 MHz to 2700 MHz
|  |  | k= | 0 | Type A |  | Type B |  | Type C
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 7.8062 | dB/Octave = | 7.8062 | dB/Octave = | 7.8062
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 57.85 | dB/decade = | 56.45 | dB/decade = | 55.5
| BS Antenna (hb in m)= | 10 | d0= | 100 | a= | 4.6 | a= | 4 | a= | 3.6
| SS Antenna (hr in m)= | 2 |  |  | X= | 10.8 | X= | 10.8 | X= | 20
|  |  | System Gain | Loss at do | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 | 78.4685 | 156.416 | 2.2254 | 156.416 | 2.4034 | 156.416 | 2.5378
0.014227
Hata-Okumura Model |  |  | Valid from 150 MHz to 1500 MHz
Lu = 69.55 + 26.16LOG(f) - 13.82*LOG(hb) - a(hr) + [44.9 - 6.55LOG(hb)]LOG(d)
a(hr) = 3.2[LOG(11.75hr)]2 - 4.97 , for 200 < f </= 1500 MHz for Large city
a(hr) = (1.1LOG(f)-0.7)hr - (1.56LOG(f)-0.8) for Small to Medium size city
Lsu = Lu - 2*[LOG(f/28)]2 - 5.4
Urban: LOG(d) = [LB - 69.55 - 26.16LOG(f) + 13.82*LOG(hb) + a(hr) ]/ [44.9 - 6.55LOG(hb)]
Suburban: LOG(d) = [LB - 69.55 - 26.16LOG(f) +13.82*LOG(hb) + a(hr) + (2*[LOG(f/28)]2 +5.4)]/ [44.9 - 6.55LOG(hb)]
d = 10LOG(d) |  |  |  |  | Urban Large City |  | Urban Small City |  | Suburban
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 7.8749 | dB/Octave = | 7.4053 | dB/Octave = | 5.2477
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 38.35 | dB/decade = | 38.35 | dB/decade = | 38.35
| BS Antenna (hb in m)= | 10 | [6 empty] | 2*[LOG(f/28)]2 + 5.4 = | 12.2737
| SS Antenna (hr in m)= | 2 |  |  | a(hr) = | 1.0454 | a(hr) = | 1.5127 | a(hr) = | 1.5127
|  |  | System Gain |  | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 |  | 157.187 | 2.6367 | 157.187 | 2.7117 | 156.416 | 5.6661
WINNER II Model |  |  | Valid from 2000 MHz to 6000 MHz
C2 Urban Macrocell N-LoS: L = [44.9 - 6.55LOG(hb)]LOG(d) + 34.46 + 5.83LOG(hb) + 23LOG(f/5) | [6 empty] | d in meters, f in GHz
C1 Suburban Macrocell N-LoS: L = [44.9 - 6.55LOG(hb)]LOG(d) + 31.46 + 5.83LOG(hb) + 23LOG(f/5)
D1 Rural Macrocell N-LoS: L = 25.1 LOG(d) + 55.4 - 0.13 LOG(hb-25) LOG(d/100) - 0.9 LOG(hr-1.5) + 21.3 LOG(f/5)
C2 Urban Macrocell N-LoS: LOG(d) = [LB - 34.46 - 5.83LOG(hb) - 23LOG(f/5)]/[44.9-6.55LOG(hb)]
C1 Suburban Macrocell N-LoS: LOG(d) = [LB - 31.46 - 5.83LOG(hb) - 23LOG(f/5)]/[44.9-6.55LOG(hb)]
D1 Rural Macrocell N-LoS: LOG(d) = [LB- 55.4 + 0.9 LOG(hr-1.5) - 21.3 LOG(f/5) - 0.13LOG(hb-25)LOG(100)]
[6 empty] | Urban |  | Suburban |  | Rural Open
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 6.9237 | dB/Octave = | 6.9237 | dB/Octave = | 6.4119
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 38.35 | dB/decade = | 38.35 | dB/decade = | #VALUE!
| BS Antenna (hb in m)= | 10 | [6 empty] | 0.13 LOG(hb-25) = | #VALUE!
| SS Antenna (hr in m)= | 2
|  |  | System Gain |  | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 |  | 157.187 | 1.9356 | 156.416 | 2.2128 | 156.416 | #VALUE!
COST231 - Hata |  |  | Valid from 1500 MHz to 2000 MHz
L = 46.3 + 33.9LOG(f) - 13.82LOG(hb) - a(hr) + [44.9-6.55LOG(hb)]*LOG(d) + C
a(hr) = 3.2[LOG(11.75hr)]2 - 4.97 and C = 3 dB for Urban
a(hr) = [1.1LOG(f)-0.7]*hr - [1.56*LOG(f)-0.8] and C = 0 dB for Suburban
LOG(d) =[ LB - 46.3 - 33.9LOG(f) + 13.82LOG(hb) + a(hr) - C ]/[44.9-6.55LOG(hb)]
[6 empty] | Urban |  | Suburban
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 10.2049 | dB/Octave = | 9.7353
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 38.35 | dB/decade = | 38.35
| BS Antenna (hb in m)= | 10 |  |  | a(hr) = | 1.0454 |  | 1.5127
| SS Antenna (hr in m)= | 2
|  |  | System Gain |  | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 |  | 157.187 | 1.918 | 156.416 | 2.2551
ITU-R M.2135-1 N-LoS |  |  | Valid from 450 MHz to 6000 MHz for Rural, 2000 MHz to 6000 MHz for Urban & Suburban
L = 161.04 – 7.1 LOG (W) + 7.5 LOG (h) - (24.37 - 3.7(h/hb)2)LOG(hb) + (43.42 - 3.1LOG(hb))*(LOG(d) - 3) + 20LOG(f) - (3.2(LOG(11.75 hr))2 -4.97) | [9 empty] | d in meters, f in GHz
LOG(d) = [LB - 161.04 +7.1 LOG (W) - 7.5 LOG (h) + (24.37 - 3.7(h/hb)2)LOG(hb) + 3(43.42 - 3.1LOG(hb)) - 20LOG(f) + (3.2(LOG(11.75 hr))2 - 4.97)]/[43.42-3.1LOG(hb)]
[6 empty] | Urban Large City |  | Urban Small City |  | Suburban |  | Rural
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 6.0206 | dB/Octave = | 6.0206 | dB/Octave = | 6.0206 | dB/Octave = | 6.0206
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 40.32 | dB/decade = | 40.32 | dB/decade = | 40.32 | dB/decade = | 40.32
| BS Antenna (hb in m)= | 10 |  |  | Avg Building Height (h) = | 30 |  | 20 |  | 8 |  | 8
| SS Antenna (hr in m)= | 2 |  |  | Avg Road Width (W) = | 20 |  | 20 |  | 20 |  | 15
|  |  | System Gain |  | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km | Link Budget | Range in km
|  |  | 163.5 |  | 157.187 | 0.32652 | 157.187 | 1.0127 | 156.416 | 2.3374 | 156.416 | 2.2219
ITU-R M.2135-1 N-LoS Urban Micro-Cell
L = 22.7 +36.7LOG(d) + 26LOG(f)
LOG(d) = [LB - 22.7 - 26LOG(f)]/36.7
Urban Micro-Cell
| Freq (MHz)= | 2000 |  | PL Frequency Dependance = | dB/Octave = | 7.8268
| Wavelength in meters = | 0.1499 |  | PL Distance dependancy = | dB/decade = | 36.7
| BS Antenna (hb in m)= | 10
| SS Antenna (hr in m)= | 2
|  |  | System Gain |  | Link Budget | Range in km
|  |  | 163.5 |  | 157.187 | 2.8264
Type A: Hilly with moderate to heavy tree density
Type B : Hilly with light tree density or flat with moderate to heavy tree density
Type C : Flat with light tree density

## 11-SNR-Chan Cap vs Range
Note: This sheet is for calculating channel capacity as function of BS-to-BS sapacing. All relevant parameters are transferred from other sheets. The sheet is not currently being used for the results on sheet C, but is retained for possible future use .
11-Signal to Noise Ratio and Channel Capacity vs. Path Length
Frequency = | 2000 | MHz |  | BS Antenna Height = | 10 | meters
System Gain = | 163.5 | dB |  | SS Antenna Height = | 2 | meters
Cell Edge SNR + 10 dB = | 23.3103 | dB |  | Terminal (SS) Location is | Outdoor |  | BS-to-BS Spacing = | 3
Re-Use Factor = | 1 |  |  | Effective DL Channel BW | 1 | MHz | Traffic Bias | DL | [13 empty] | MAC and Control Channel OH = | 30.9% |  |  |  |  | MAC and Control Channel OH = | 29.3%
| Urban Large City | Urban Small City | Suburban | Rural | Rural Open | Type A | Type B | Type C | [13 empty] | Channel BW in MHz = | 1 |  |  |  |  | Channel BW in MHz = | 1
Total Margin = | 6.313 | 6.313 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 | [9 empty] | Mod/Coding | Mod Eff | Coding | Req S/N* | UL SE | UL Bit Rate (Mbps) | Mod/Coding | Mod Eff | Coding | Req S/N* | DL SE | DL Bit Rate (Mbps)
Link Budget = | 157.187 | 157.187 | 156.416 | 156.416 | 156.416 | 156.416 | 156.416 | 156.416 | [9 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Estimated Range (D in km) | [17 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | [9 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Erceg-SUI -Modified | [5 empty] | 2.2254 | 2.4034 | 2.5378 | [9 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Erceg-SUI-Original | [5 empty] | 2.2254 | 2.4034 | 2.5378 | [9 empty] | QPSK | 2 | 0.083333 | 5.7 | 0.16667 | 0.11517 | QPSK | 2 | 0.083333 | 5.7 | 0.16667 | 0.11783
Hata-Okumura | n/a | n/a | n/a | [14 empty] | QPSK | 2 | 0.125 | 7.5 | 0.25 | 0.17275 | QPSK | 2 | 0.125 | 7.5 | 0.25 | 0.17675
COST231-Hata | n/a |  | n/a | [14 empty] | QPSK | 2 | 0.25 | 10.5 | 0.5 | 0.3455 | QPSK | 2 | 0.25 | 10.5 | 0.5 | 0.3535
WINNER II | n/a |  | n/a |  | n/a | [12 empty] | QPSK | 2 | 0.5 | 13.5 | 1 | 0.691 | QPSK | 2 | 0.5 | 13.5 | 1 | 0.707
ITU-R M.2135-1 | n/a | n/a | 2.3374 | 2.2219 | [13 empty] | QPSK | 2 | 0.75 | 16.8 | 1.5 | 1.0365 | QPSK | 2 | 0.75 | 16.8 | 1.5 | 1.0605
ITU-R M.2135-1 Urban Micro-Cell | 2.8264 | [16 empty] | 16QAM | 4 | 0.5 | 18.9 | 2 | 1.382 | 16QAM | 4 | 0.5 | 18.9 | 2 | 1.414
UL Channel/Sector Data Rate at Maximum Range D in Mbps |  |  |  | (Note: Excludes MAC and control OH) | [13 empty] | 16QAM | 4 | 0.75 | 23 | 3 | 2.073 | 16QAM | 4 | 0.25 | 23 | 1 | 0.707
Erceg-SUI -Modified | [5 empty] | #VALUE! | #VALUE! | #VALUE! | [9 empty] | 64QAM | 6 | 0.5 | 23.9 | 3 | 2.073 | 64QAM | 6 | 0.5 | 23.9 | 3 | 2.121
Erceg-SUI-Original | [17 empty] | 64QAM | 6 | 0.66667 | 27.3 | 4 | 2.764 | 64QAM | 6 | 0.66667 | 27.3 | 4 | 2.828
Hata-Okumura | n/a | n/a | n/a | [14 empty] | 64QAM | 6 | 0.75 | 28.5 | 4.5 | 3.1095 | 64QAM | 6 | 0.75 | 28.5 | 4.5 | 3.1815
COST231-Hata | n/a |  | n/a | [14 empty] | 64QAM | 6 | 0.83333 | 30.3 | 5 | 3.455 | 64QAM | 6 | 0.83333 | 30.3 | 5 | 3.535
WINNER II | n/a |  | n/a |  | n/a
ITU-R M.2135-1 | n/a | n/a | #VALUE! | #VALUE!
ITU-R M.2135-1 Urban Micro-Cell | #VALUE!
UL Cell Data Rate in Mbps at BS-to-BS Spacing = |  | 3 | km | (Note: Excludes MAC and control OH)
Erceg-SUI -Modified | [5 empty] | #VALUE! | #VALUE! | #VALUE!
Erceg-SUI-Original
Hata-Okumura | n/a | n/a | n/a
COST231-Hata | n/a |  | n/a
WINNER II | n/a |  | n/a |  | n/a
ITU-R M.2135-1 | n/a | n/a | #VALUE! | #VALUE!
ITU-R M.2135-1 Urban Micro-Cell | #VALUE!
Total Path Loss distance dependancy (dB per Decade)
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C
Erceg-SUI -Modified | [5 empty] | 57.85 | 56.45 | 55.5
Erceg-SUI-Original | [5 empty] | 57.85 | 56.45 | 55.5
Hata-Okumura | n/a | n/a | n/a
COST231-Hata | n/a |  | n/a
WINNER II | n/a |  | n/a |  | n/a
ITU-R M.2135-1 | n/a | n/a | 40.32 | 40.32
ITU-R M.2135-1 Urban Micro-Cell | 36.7
Erceg-SUI -Modified | Type A | 57.85 | dB/Decade |  |  | Type B | 56.45 | dB/Decade |  |  | Type C | 55.5 | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.1 | 101.2578 | #VALUE! | #VALUE! | 0.2019% | 0.1 | 101.2578 | #VALUE! | #VALUE! | 0.1731% | 0.1 | 101.2578 | #VALUE! | #VALUE! | 0.1553%
1 | 0.45574 | 63.1512 | #VALUE! | #VALUE! | 4.194% | 0.49056 | 62.2681 | #VALUE! | #VALUE! | 4.166% | 0.51693 | 61.6622 | #VALUE! | #VALUE! | 4.149%
2 | 0.6367 | 54.7501 | #VALUE! | #VALUE! | 8.186% | 0.68652 | 54.0289 | #VALUE! | #VALUE! | 8.159% | 0.72418 | 53.5363 | #VALUE! | #VALUE! | 8.143%
3 | 0.77659 | 49.7603 | #VALUE! | #VALUE! | 12.18% | 0.83783 | 49.1458 | #VALUE! | #VALUE! | 12.15% | 0.88412 | 48.7266 | #VALUE! | #VALUE! | 12.14%
4 | 0.89487 | 46.1987 | #VALUE! | #VALUE! | 16.17% | 0.96572 | 45.6631 | #VALUE! | #VALUE! | 16.15% | 1.0193 | 45.2981 | #VALUE! | #VALUE! | 16.13%
5 | 0.99924 | 43.427 | #VALUE! | #VALUE! | 20.16% | 1.0785 | 42.9541 | #VALUE! | #VALUE! | 20.14% | 1.1385 | 42.6321 | #VALUE! | #VALUE! | 20.12%
6 | 1.0937 | 41.1576 | #VALUE! | #VALUE! | 24.15% | 1.1806 | 40.7368 | #VALUE! | #VALUE! | 24.13% | 1.2463 | 40.4503 | #VALUE! | #VALUE! | 24.12%
7 | 1.1806 | 39.2362 | #VALUE! | #VALUE! | 28.15% | 1.2746 | 38.8598 | #VALUE! | #VALUE! | 28.12% | 1.3456 | 38.6036 | #VALUE! | #VALUE! | 28.11%
8 | 1.2616 | 37.5701 | #VALUE! | #VALUE! | 32.14% | 1.3621 | 37.2324 | #VALUE! | #VALUE! | 32.12% | 1.438 | 37.0027 | #VALUE! | #VALUE! | 32.11%
9 | 1.3376 | 36.0992 | #VALUE! | #VALUE! | 36.13% | 1.4443 | 35.796 | #VALUE! | #VALUE! | 36.11% | 1.5248 | 35.5897 | #VALUE! | #VALUE! | 36.1%
10 | 1.4096 | 34.7827 | #VALUE! | #VALUE! | 40.12% | 1.522 | 34.5104 | #VALUE! | #VALUE! | 40.1% | 1.6069 | 34.3251 | #VALUE! | #VALUE! | 40.09%
11 | 1.4781 | 33.5912 | #VALUE! | #VALUE! | 44.11% | 1.596 | 33.3469 | #VALUE! | #VALUE! | 44.1% | 1.6851 | 33.1807 | #VALUE! | #VALUE! | 44.09%
12 | 1.5435 | 32.5029 | #VALUE! | #VALUE! | 48.1% | 1.6667 | 32.2843 | #VALUE! | #VALUE! | 48.09% | 1.7597 | 32.1356 | #VALUE! | #VALUE! | 48.08%
13 | 1.6063 | 31.5015 | #VALUE! | #VALUE! | 52.1% | 1.7345 | 31.3065 | #VALUE! | #VALUE! | 52.08% | 1.8314 | 31.1739 | #VALUE! | #VALUE! | 52.07%
14 | 1.6667 | 30.574 | #VALUE! | #VALUE! | 56.09% | 1.7998 | 30.401 | #VALUE! | #VALUE! | 56.08% | 1.9003 | 30.2834 | #VALUE! | #VALUE! | 56.07%
15 | 1.7249 | 29.7104 | #VALUE! | #VALUE! | 60.08% | 1.8627 | 29.5578 | #VALUE! | #VALUE! | 60.07% | 1.9668 | 29.4541 | #VALUE! | #VALUE! | 60.06%
16 | 1.7813 | 28.9023 | #VALUE! | #VALUE! | 64.07% | 1.9236 | 28.7689 | #VALUE! | #VALUE! | 64.06% | 2.0311 | 28.6783 | #VALUE! | #VALUE! | 64.06%
17 | 1.836 | 28.143 | #VALUE! | #VALUE! | 68.06% | 1.9827 | 28.0278 | #VALUE! | #VALUE! | 68.06% | 2.0935 | 27.9494 | #VALUE! | #VALUE! | 68.05%
18 | 1.8891 | 27.4271 | #VALUE! | #VALUE! | 72.06% | 2.04 | 27.3288 | #VALUE! | #VALUE! | 72.05% | 2.1541 | 27.262 | #VALUE! | #VALUE! | 72.04%
19 | 1.9407 | 26.7498 | #VALUE! | #VALUE! | 76.05% | 2.0958 | 26.6676 | #VALUE! | #VALUE! | 76.04% | 2.213 | 26.6118 | #VALUE! | #VALUE! | 76.04%
20 | 1.991 | 26.1071 | #VALUE! | #VALUE! | 80.04% | 2.1501 | 26.0403 | #VALUE! | #VALUE! | 80.03% | 2.2703 | 25.9949 | #VALUE! | #VALUE! | 80.03%
21 | 2.04 | 25.4957 | #VALUE! | #VALUE! | 84.03% | 2.2031 | 25.4435 | #VALUE! | #VALUE! | 84.03% | 2.3263 | 25.408 | #VALUE! | #VALUE! | 84.02%
22 | 2.0879 | 24.9127 | #VALUE! | #VALUE! | 88.02% | 2.2548 | 24.8744 | #VALUE! | #VALUE! | 88.02% | 2.3809 | 24.8484 | #VALUE! | #VALUE! | 88.02%
23 | 2.1347 | 24.3555 | #VALUE! | #VALUE! | 92.02% | 2.3054 | 24.3305 | #VALUE! | #VALUE! | 92.01% | 2.4344 | 24.3136 | #VALUE! | #VALUE! | 92.01%
24 | 2.1805 | 23.822 | #VALUE! | #VALUE! | 96.01% | 2.3549 | 23.8098 | #VALUE! | #VALUE! | 96.01% | 2.4866 | 23.8015 | #VALUE! | #VALUE! | 96.01%
25 | 2.2254 | 23.3103 | #VALUE! | #VALUE! | 100% | 2.4034 | 23.3103 | #VALUE! | #VALUE! | 100% | 2.5378 | 23.3103 | #VALUE! | #VALUE! | 100%
Hata-Okumura | Large City Urban | n/a | dB/Decade |  |  | Small City Urban | n/a | dB/Decade |  |  | Suburban | n/a | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
25 | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE!
COST231-Hata | Large City Urban | n/a | dB/Decade |  |  | Suburban | n/a | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
25 | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE!
WINNER II | Large City Urban | n/a | dB/Decade |  |  | Suburban | n/a | dB/Decade |  |  | Rural Open | n/a | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
25 | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE!
ITU-R M.2135-1 | Large City Urban | n/a | dB/Decade |  |  | Small City Urban | n/a | dB/Decade |  |  | Suburban | 40.32 | dB/Decade |  |  | Rural | 40.32 | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area | d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.05 | 90.6348 | #VALUE! | #VALUE! | 0.04576% | 0.05 | 89.7477 | #VALUE! | #VALUE! | 0.05064%
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.47003 | 51.3971 | #VALUE! | #VALUE! | 4.044% | 0.44707 | 51.387 | #VALUE! | #VALUE! | 4.049%
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.66284 | 45.3781 | #VALUE! | #VALUE! | 8.042% | 0.63028 | 45.3732 | #VALUE! | #VALUE! | 8.047%
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.81104 | 41.8447 | #VALUE! | #VALUE! | 12.04% | 0.77112 | 41.8416 | #VALUE! | #VALUE! | 12.04%
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.93606 | 39.3342 | #VALUE! | #VALUE! | 16.04% | 0.88994 | 39.332 | #VALUE! | #VALUE! | 16.04%
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.0463 | 37.3855 | #VALUE! | #VALUE! | 20.04% | 0.99467 | 37.3838 | #VALUE! | #VALUE! | 20.04%
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1459 | 35.7926 | #VALUE! | #VALUE! | 24.03% | 1.0894 | 35.7912 | #VALUE! | #VALUE! | 24.04%
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2375 | 34.4453 | #VALUE! | #VALUE! | 28.03% | 1.1765 | 34.4442 | #VALUE! | #VALUE! | 28.04%
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3229 | 33.278 | #VALUE! | #VALUE! | 32.03% | 1.2576 | 33.2771 | #VALUE! | #VALUE! | 32.03%
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.403 | 32.2481 | #VALUE! | #VALUE! | 36.03% | 1.3337 | 32.2474 | #VALUE! | #VALUE! | 36.03%
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4788 | 31.3268 | #VALUE! | #VALUE! | 40.03% | 1.4058 | 31.3261 | #VALUE! | #VALUE! | 40.03%
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5509 | 30.4932 | #VALUE! | #VALUE! | 44.03% | 1.4743 | 30.4927 | #VALUE! | #VALUE! | 44.03%
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6198 | 29.7321 | #VALUE! | #VALUE! | 48.02% | 1.5398 | 29.7317 | #VALUE! | #VALUE! | 48.03%
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6858 | 29.032 | #VALUE! | #VALUE! | 52.02% | 1.6026 | 29.0316 | #VALUE! | #VALUE! | 52.02%
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7494 | 28.3837 | #VALUE! | #VALUE! | 56.02% | 1.663 | 28.3833 | #VALUE! | #VALUE! | 56.02%
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8108 | 27.7801 | #VALUE! | #VALUE! | 60.02% | 1.7214 | 27.7798 | #VALUE! | #VALUE! | 60.02%
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8701 | 27.2155 | #VALUE! | #VALUE! | 64.02% | 1.7778 | 27.2152 | #VALUE! | #VALUE! | 64.02%
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9276 | 26.685 | #VALUE! | #VALUE! | 68.01% | 1.8324 | 26.6848 | #VALUE! | #VALUE! | 68.02%
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9835 | 26.1849 | #VALUE! | #VALUE! | 72.01% | 1.8855 | 26.1848 | #VALUE! | #VALUE! | 72.01%
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.0378 | 25.7118 | #VALUE! | #VALUE! | 76.01% | 1.9372 | 25.7117 | #VALUE! | #VALUE! | 76.01%
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.0907 | 25.263 | #VALUE! | #VALUE! | 80.01% | 1.9875 | 25.2629 | #VALUE! | #VALUE! | 80.01%
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1423 | 24.8361 | #VALUE! | #VALUE! | 84.01% | 2.0365 | 24.836 | #VALUE! | #VALUE! | 84.01%
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1927 | 24.429 | #VALUE! | #VALUE! | 88.01% | 2.0844 | 24.4289 | #VALUE! | #VALUE! | 88.01%
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.242 | 24.04 | #VALUE! | #VALUE! | 92% | 2.1312 | 24.04 | #VALUE! | #VALUE! | 92%
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2902 | 23.6675 | #VALUE! | #VALUE! | 96% | 2.177 | 23.6675 | #VALUE! | #VALUE! | 96%
25 | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | n/a | 23.3103 | #VALUE! | #VALUE! | #VALUE! | 2.3374 | 23.3103 | #VALUE! | #VALUE! | 100% | 2.2219 | 23.3103 | #VALUE! | #VALUE! | 100%
ITU-R M.2135-1 Urban Micro-Cell | Large City Urban | 36.7 | dB/Decade
| d | Relative SnR in dB | UL Bit Rate (Mbps) | UL Channel Capacity Mbps | Rel Coverage Area
0 | 0.05 | 87.6183 | #VALUE! | #VALUE! | 0.0313%
1 | 0.5674 | 48.9029 | #VALUE! | #VALUE! | 4.03%
2 | 0.80086 | 43.41 | #VALUE! | #VALUE! | 8.029%
3 | 0.98021 | 40.1891 | #VALUE! | #VALUE! | 12.03%
4 | 1.1315 | 37.9016 | #VALUE! | #VALUE! | 16.03%
5 | 1.2648 | 36.1264 | #VALUE! | #VALUE! | 20.03%
6 | 1.3853 | 34.6755 | #VALUE! | #VALUE! | 24.02%
7 | 1.4962 | 33.4485 | #VALUE! | #VALUE! | 28.02%
8 | 1.5994 | 32.3855 | #VALUE! | #VALUE! | 32.02%
9 | 1.6963 | 31.4477 | #VALUE! | #VALUE! | 36.02%
10 | 1.788 | 30.6088 | #VALUE! | #VALUE! | 40.02%
11 | 1.8752 | 29.8498 | #VALUE! | #VALUE! | 44.02%
12 | 1.9585 | 29.1568 | #VALUE! | #VALUE! | 48.02%
13 | 2.0384 | 28.5193 | #VALUE! | #VALUE! | 52.02%
14 | 2.1153 | 27.9291 | #VALUE! | #VALUE! | 56.01%
15 | 2.1895 | 27.3796 | #VALUE! | #VALUE! | 60.01%
16 | 2.2613 | 26.8655 | #VALUE! | #VALUE! | 64.01%
17 | 2.3309 | 26.3826 | #VALUE! | #VALUE! | 68.01%
18 | 2.3984 | 25.9273 | #VALUE! | #VALUE! | 72.01%
19 | 2.4641 | 25.4966 | #VALUE! | #VALUE! | 76.01%
20 | 2.5281 | 25.088 | #VALUE! | #VALUE! | 80.01%
21 | 2.5905 | 24.6993 | #VALUE! | #VALUE! | 84.01%
22 | 2.6514 | 24.3287 | #VALUE! | #VALUE! | 88%
23 | 2.711 | 23.9746 | #VALUE! | #VALUE! | 92%
24 | 2.7693 | 23.6355 | #VALUE! | #VALUE! | 96%
25 | 2.8264 | 23.3103 | #VALUE! | #VALUE! | 100%
All of these values, except BS-to-BS spacing, transfer from Worksheet 1, 1a, or 2
Uplink channel or sector data rate at maximum range
Uplink cell data rate for a specific BS-to-BS spacing assuming 3-sector cell site

## 12-SNR-Chan SE vs Range
Note: This sheet is for calculating Channel Spectral Efficiency relative to path length, all relevant AT parameters are transferred from other sheets.
12-Signal to Noise Ratio and Channel Spectral Efficiency vs. Path Length
Frequency = | 2000 | MHz |  | BS Antenna Height = | 10 | meters
System Gain = | 163.5 | dB |  | SS Antenna Height = | 2 | meters
Cell Edge SNR + 10 dB = | 23.3103 | dB |  | Terminal (SS) Location is | Outdoor |  | Required Cell SE Density= | 0.23562
Re-Use Factor = | 1 |  |  | Effective DL Channel BW = | 1 | MHz | Traffic Bias | DL
| Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | [16 empty] | UL Channel BW in MHz = | 1 |  |  |  |  | DL Channel BW in MHz = | 1
Total Margin = | 6.313 | 6.313 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 | 7.084 | [12 empty] | UL Mod/Coding | UL Mod Eff | DL Coding | Req UL S/N* | UL SE | UL Bit Rate (Mbps) | DL Mod/Coding | DL Mod Eff | DL Coding | Req DL S/N* | DL SE | DL Bit Rate (Mbps)
Link Budget = | 157.187 | 157.187 | 156.416 | 156.416 | 156.416 | 156.416 | 156.416 | 156.416 | [12 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Estimated Range (D in km) | [20 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C | [12 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Erceg-SUI-Modified | n/a | n/a | n/a | n/a | n/a | 2.2254 | 2.4034 | 2.5378 | [12 empty] | n/a | 0 | 0 | 5.7 | 0 | 0 | n/a | 0 | 0 | 5.7 | 0 | 0
Erceg-SUI-Original | n/a | n/a | n/a | n/a | n/a | 2.2254 | 2.4034 | 2.5378 | [12 empty] | QPSK | 2 | 0.083333 | 5.7 | 0.16667 | 0.16667 | QPSK | 2 | 0.083333 | 5.7 | 0.16667 | 0.16667
Hata-Okumura | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | [12 empty] | QPSK | 2 | 0.125 | 7.5 | 0.25 | 0.25 | QPSK | 2 | 0.125 | 7.5 | 0.25 | 0.25
COST231-Hata | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | [12 empty] | QPSK | 2 | 0.25 | 10.5 | 0.5 | 0.5 | QPSK | 2 | 0.25 | 10.5 | 0.5 | 0.5
WINNER II | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | [12 empty] | QPSK | 2 | 0.5 | 13.5 | 1 | 1 | QPSK | 2 | 0.5 | 13.5 | 1 | 1
ITU-R M.2135-1 | n/a | n/a | 2.3374 | 2.2219 | n/a | n/a | n/a | n/a | [12 empty] | QPSK | 2 | 0.75 | 16.8 | 1.5 | 1.5 | QPSK | 2 | 0.75 | 16.8 | 1.5 | 1.5
ITU-R M.2135-1 Urban Micro-Cell | 2.8264 | [19 empty] | 16QAM | 4 | 0.5 | 18.9 | 2 | 2 | 16QAM | 4 | 0.5 | 18.9 | 2 | 2
UL Cell SE Density at Maximum Range D in bps/Hz/sq-km |  |  |  | (Note: Excludes MAC and control OH) | [16 empty] | 16QAM | 4 | 0.75 | 23 | 3 | 3 | 16QAM | 4 | 0.25 | 23 | 1 | 1
Erceg-SUI-Modified | n/a | n/a | n/a | n/a | n/a | 0.32331 | 0.2772 | 0.24503 | [12 empty] | 64QAM | 6 | 0.5 | 23.9 | 3 | 3 | 64QAM | 6 | 0.5 | 23.9 | 3 | 3
Erceg-SUI-Original | n/a | n/a | n/a | n/a | n/a | [15 empty] | 64QAM | 6 | 0.66667 | 27.3 | 4 | 4 | 64QAM | 6 | 0.66667 | 27.3 | 4 | 4
Hata-Okumura | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | [12 empty] | 64QAM | 6 | 0.75 | 28.5 | 4.5 | 4.5 | 64QAM | 6 | 0.75 | 28.5 | 4.5 | 4.5
COST231-Hata | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | [12 empty] | 64QAM | 6 | 0.83333 | 30.3 | 5 | 5 | 64QAM | 6 | 0.83333 | 30.3 | 5 | 5
WINNER II | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
ITU-R M.2135-1 | n/a | n/a | 0.27618 | 0.3181 | n/a | n/a | n/a | n/a
ITU-R M.2135-1 Urban Micro-Cell | 0.18791
Range for Required UL SE Density= | 0.23562 | bps/Hz/sq-km |  | (Note: Excludes MAC and control OH)
Erceg-SUI-Modified | n/a | n/a | n/a | n/a | n/a | 2.2254 | 2.4034 | 2.5378
Erceg-SUI-Original | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Hata-Okumura | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
COST231-Hata | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
WINNER II | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
ITU-R M.2135-1 | n/a | n/a | 2.3374 | 2.2219 | n/a | n/a | n/a | n/a
ITU-R M.2135-1 Urban Micro-Cell | 2.6514
Total Path Loss distance dependancy (dB per Decade)
Path Loss Model | Large City Urban | Small City Urban | Suburban | Rural | Rural Open | Type A | Type B | Type C
Erceg-SUI -Modified | [5 empty] | 57.85 | 56.45 | 55.5
Erceg-SUI-Original | [5 empty] | 57.85 | 56.45 | 55.5
Hata-Okumura | n/a | n/a | n/a
COST231-Hata | n/a |  | n/a
WINNER II | n/a |  | n/a |  | n/a
ITU-R M.2135-1 | n/a | n/a | 40.32 | 40.32
ITU-R M.2135-1 Urban Micro-Cell | 36.7
Erceg-SUI -Modified | Type A | 57.85 | dB/Decade |  |  |  | Type B | 56.45 | dB/Decade |  |  |  | Type C | 55.5 | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | 2.2254 | 23.3103 | 1 | 0.32331 | 2.2254 | 100% | 2.4034 | 23.3103 | 1 | 0.2772 | 2.4034 | 100% | 2.5378 | 23.3103 | 1 | 0.24503 | 2.5378 | 100%
24 | 2.1805 | 23.822 | 1 | 0.34742 | 2.1805 | 96.01% | 2.3549 | 23.8098 | 1 | 0.29787 | 2.3549 | 96.01% | 2.4866 | 23.8015 | 1 | 0.26326 | 2.4866 | 96.01%
23 | 2.1346 | 24.3566 | 3 | 0.37461 | 2.1346 | 92.01% | 2.3054 | 24.3305 | 3 | 0.32116 | 2.3054 | 92.01% | 2.4344 | 24.3136 | 3 | 0.2838 | 2.4344 | 92.01%
22 | 2.0878 | 24.9138 | 3 | 0.39736 | 2.0878 | 88.02% | 2.2548 | 24.8744 | 3 | 0.34066 | 2.2548 | 88.02% | 2.3809 | 24.8484 | 3 | 0.30091 | 2.3809 | 88.02%
21 | 2.0399 | 25.4969 | 3 | 0.42284 | 2.0399 | 84.02% | 2.2031 | 25.4435 | 3 | 0.36252 | 2.2031 | 84.03% | 2.3263 | 25.408 | 3 | 0.32006 | 2.3263 | 84.02%
20 | 1.9909 | 26.1084 | 3 | 0.45156 | 1.9909 | 80.03% | 2.1501 | 26.0403 | 3 | 0.38715 | 2.1501 | 80.03% | 2.2703 | 25.9949 | 3 | 0.34163 | 2.2703 | 80.03%
19 | 1.9406 | 26.7511 | 3 | 0.48415 | 1.9406 | 76.04% | 2.0958 | 26.6676 | 3 | 0.41508 | 2.0958 | 76.04% | 2.213 | 26.6118 | 3 | 0.36609 | 2.213 | 76.04%
18 | 1.8889 | 27.4285 | 4 | 0.52138 | 1.8889 | 72.05% | 2.04 | 27.3288 | 4 | 0.44701 | 2.04 | 72.05% | 2.1541 | 27.262 | 3 | 0.39403 | 2.1541 | 72.04%
17 | 1.8359 | 28.1445 | 4 | 0.55756 | 1.8359 | 68.06% | 1.9827 | 28.0278 | 4 | 0.47804 | 1.9827 | 68.06% | 2.0935 | 27.9494 | 4 | 0.42619 | 2.0935 | 68.05%
16 | 1.7812 | 28.9039 | 4.5 | 0.59899 | 1.7812 | 64.06% | 1.9236 | 28.7689 | 4.5 | 0.51357 | 1.9236 | 64.06% | 2.0311 | 28.6783 | 4.5 | 0.45774 | 2.0311 | 64.06%
15 | 1.7248 | 29.7121 | 4.5 | 0.64257 | 1.7248 | 60.07% | 1.8627 | 29.5578 | 4.5 | 0.55095 | 1.8627 | 60.07% | 1.9668 | 29.4541 | 4.5 | 0.49087 | 1.9668 | 60.06%
14 | 1.6665 | 30.5759 | 5 | 0.69293 | 1.6665 | 56.08% | 1.7998 | 30.401 | 5 | 0.59414 | 1.7998 | 56.08% | 1.9003 | 30.2834 | 4.5 | 0.52914 | 1.9003 | 56.07%
13 | 1.6061 | 31.5035 | 5 | 0.74603 | 1.6061 | 52.09% | 1.7345 | 31.3065 | 5 | 0.63969 | 1.7345 | 52.08% | 1.8314 | 31.1739 | 5 | 0.57382 | 1.8314 | 52.07%
12 | 1.5434 | 32.5051 | 5 | 0.80795 | 1.5434 | 48.1% | 1.6667 | 32.2843 | 5 | 0.69281 | 1.6667 | 48.09% | 1.7597 | 32.1356 | 5 | 0.62148 | 1.7597 | 48.08%
11 | 1.4779 | 33.5935 | 5 | 0.88108 | 1.4779 | 44.1% | 1.596 | 33.3469 | 5 | 0.75555 | 1.596 | 44.1% | 1.6851 | 33.1807 | 5 | 0.67778 | 1.6851 | 44.09%
10 | 1.4095 | 34.7853 | 5 | 0.96876 | 1.4095 | 40.11% | 1.522 | 34.5104 | 5 | 0.83077 | 1.522 | 40.1% | 1.6069 | 34.3251 | 5 | 0.74529 | 1.6069 | 40.09%
9 | 1.3375 | 36.102 | 5 | 1.0758 | 1.3375 | 36.12% | 1.4443 | 35.796 | 5 | 0.92264 | 1.4443 | 36.11% | 1.5248 | 35.5897 | 5 | 0.82775 | 1.5248 | 36.1%
8 | 1.2614 | 37.5732 | 5 | 1.2095 | 1.2614 | 32.13% | 1.3621 | 37.2324 | 5 | 1.0373 | 1.3621 | 32.12% | 1.438 | 37.0027 | 5 | 0.93072 | 1.438 | 32.11%
7 | 1.1805 | 39.2398 | 5 | 1.3811 | 1.1805 | 28.14% | 1.2746 | 38.8598 | 5 | 1.1846 | 1.2746 | 28.12% | 1.3456 | 38.6036 | 5 | 1.0629 | 1.3456 | 28.11%
6 | 1.0935 | 41.1618 | 5 | 1.6094 | 1.0935 | 24.15% | 1.1806 | 40.7368 | 5 | 1.3806 | 1.1806 | 24.13% | 1.2463 | 40.4503 | 5 | 1.239 | 1.2463 | 24.12%
5 | 0.99904 | 43.432 | 5 | 1.9282 | 0.99904 | 20.15% | 1.0785 | 42.9541 | 5 | 1.6544 | 1.0785 | 20.14% | 1.1385 | 42.6321 | 5 | 1.4848 | 1.1385 | 20.12%
4 | 0.89464 | 46.2049 | 5 | 2.4045 | 0.89464 | 16.16% | 0.96572 | 45.6631 | 5 | 2.0636 | 0.96572 | 16.15% | 1.0193 | 45.2981 | 5 | 1.8525 | 1.0193 | 16.13%
3 | 0.77633 | 49.7687 | 5 | 3.1932 | 0.77633 | 12.17% | 0.83783 | 49.1458 | 5 | 2.7416 | 0.83783 | 12.15% | 0.88412 | 48.7266 | 5 | 2.4621 | 0.88412 | 12.14%
2 | 0.63639 | 54.7625 | 5 | 4.7519 | 0.63639 | 8.178% | 0.68652 | 54.0289 | 5 | 4.0834 | 0.68652 | 8.159% | 0.72418 | 53.5363 | 5 | 3.6696 | 0.72418 | 8.143%
1 | 0.4553 | 63.1755 | 5 | 9.2838 | 0.4553 | 4.186% | 0.49056 | 62.2681 | 5 | 7.997 | 0.49056 | 4.166% | 0.51693 | 61.6622 | 5 | 7.2019 | 0.51693 | 4.149%
0 | 0.1 | 101.2578 | 5 |  | 0.1 | 0.2019% | 0.1 | 101.2578 | 5 |  | 0.1 | 0.1731% | 0.1 | 101.2578 | 5 |  | 0.1 | 0.1553%
Hata-Okumura | Large City Urban | n/a | dB/Decade |  |  |  | Small City Urban | n/a | dB/Decade |  |  |  | Suburban | n/a | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE!
COST231-Hata | Large City Urban | n/a | dB/Decade |  |  |  | Suburban | n/a | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE!
WINNER II | Large City Urban | n/a | dB/Decade |  |  |  | Suburban | n/a | dB/Decade |  |  |  | Rural Open | n/a | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE!
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE!
ITU-R M.2135-1 | Large City Urban | n/a | dB/Decade |  |  |  | Small City Urban | n/a | dB/Decade |  |  |  | Suburban | 40.32 | dB/Decade |  |  |  | Rural | 40.32 | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area | d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | n/a | 23.3103 | 1 | #VALUE! | n/a | #VALUE! | 2.3374 | 23.3103 | 1 | 0.27618 | 2.3374 | 100% | 2.2219 | 23.3103 | 3 | 0.3181 | 2.2219 | 100%
24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2901 | 23.6677 | 1 | 0.29661 | 2.2901 | 96% | 2.177 | 23.6677 | 3 | 0.33501 | 2.177 | 96%
23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.2419 | 24.0403 | 3 | 0.31963 | 2.2419 | 92% | 2.1312 | 24.0403 | 3 | 0.35372 | 2.1312 | 92%
22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1926 | 24.4295 | 3 | 0.33844 | 2.1926 | 88% | 2.0843 | 24.4295 | 3 | 0.37452 | 2.0843 | 88%
21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1422 | 24.8368 | 3 | 0.35945 | 2.1422 | 84% | 2.0364 | 24.8368 | 3 | 0.39778 | 2.0364 | 84%
20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.0906 | 25.264 | 3 | 0.38309 | 2.0906 | 80% | 1.9873 | 25.264 | 3 | 0.42393 | 1.9873 | 80%
19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.0377 | 25.7131 | 3 | 0.40984 | 2.0377 | 76% | 1.937 | 25.7131 | 3 | 0.45354 | 1.937 | 76%
18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9833 | 26.1865 | 3 | 0.44033 | 1.9833 | 72% | 1.8853 | 26.1865 | 3 | 0.48728 | 1.8853 | 72%
17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9274 | 26.6869 | 3 | 0.47537 | 1.9274 | 68% | 1.8322 | 26.6869 | 3 | 0.52606 | 1.8322 | 68%
16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8699 | 27.2177 | 3 | 0.51601 | 1.8699 | 64% | 1.7775 | 27.2177 | 3 | 0.57103 | 1.7775 | 64%
15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8105 | 27.7828 | 4 | 0.56362 | 1.8105 | 60% | 1.7211 | 27.7828 | 4 | 0.62372 | 1.7211 | 60%
14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7491 | 28.3868 | 4 | 0.61107 | 1.7491 | 56% | 1.6627 | 28.3868 | 4 | 0.67623 | 1.6627 | 56%
13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6855 | 29.0357 | 4.5 | 0.66701 | 1.6855 | 52% | 1.6022 | 29.0357 | 4.5 | 0.73813 | 1.6022 | 52%
12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.6194 | 29.7365 | 4.5 | 0.72777 | 1.6194 | 48% | 1.5394 | 29.7365 | 4.5 | 0.80537 | 1.5394 | 48%
11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.5504 | 30.4983 | 5 | 0.8006 | 1.5504 | 44% | 1.4738 | 30.4983 | 5 | 0.88597 | 1.4738 | 44%
10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4783 | 31.3328 | 5 | 0.88066 | 1.4783 | 40% | 1.4053 | 31.3328 | 5 | 0.97456 | 1.4053 | 40%
9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.4024 | 32.2552 | 5 | 0.97851 | 1.4024 | 36% | 1.3331 | 32.2552 | 5 | 1.0828 | 1.3331 | 36%
8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.3222 | 33.2865 | 5 | 1.1008 | 1.3222 | 32% | 1.2569 | 33.2865 | 5 | 1.2182 | 1.2569 | 32%
7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.2368 | 34.4556 | 5 | 1.2581 | 1.2368 | 28% | 1.1757 | 34.4556 | 5 | 1.3922 | 1.1757 | 28%
6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.1451 | 35.8052 | 5 | 1.4678 | 1.1451 | 24% | 1.0885 | 35.8052 | 5 | 1.6243 | 1.0885 | 24%
5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.0453 | 37.4015 | 5 | 1.7613 | 1.0453 | 20% | 0.99366 | 37.4015 | 5 | 1.9491 | 0.99366 | 20%
4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.93494 | 39.3552 | 5 | 2.2017 | 0.93494 | 16% | 0.88876 | 39.3552 | 5 | 2.4364 | 0.88876 | 16%
3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.80968 | 41.874 | 5 | 2.9355 | 0.80968 | 12% | 0.76969 | 41.874 | 5 | 3.2485 | 0.76969 | 12%
2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.6611 | 45.424 | 5 | 4.4033 | 0.6611 | 8% | 0.62845 | 45.424 | 5 | 4.8728 | 0.62845 | 8%
1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.46747 | 51.4928 | 5 | 8.8066 | 0.46747 | 4% | 0.44438 | 51.4928 | 5 | 9.7456 | 0.44438 | 4%
0 | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | #VALUE! | #VALUE! |  | 0.05 | #VALUE! | 0.05 | 90.6348 | 5 |  | 0.05 | 0.04576% | 0.05 | 89.7477 | 5 |  | 0.05 | 0.05064%
ITU-R M.2135-1 Urban Micro-Cell | Urban Micr-Cell | 36.7 | dB/Decade
| d | Relative SnR in dB | DL SE (bps/Hz) | Cell SE Density bps/Hz/sq-km | d | Rel Coverage Area
25 | 2.8264 | 23.3103 | 1 | 0.18791 | 2.8264 | 100%
24 | 2.7693 | 23.6355 | 1 | 0.2018 | 2.7693 | 96%
23 | 2.711 | 23.9746 | 3 | 0.21745 | 2.711 | 92%
22 | 2.6514 | 24.3287 | 3 | 0.2302 | 2.6514 | 88%
21 | 2.5905 | 24.6993 | 3 | 0.24445 | 2.5905 | 84.01%
20 | 2.5281 | 25.088 | 3 | 0.26046 | 2.5281 | 80.01%
19 | 2.4641 | 25.4966 | 3 | 0.27859 | 2.4641 | 76.01%
18 | 2.3984 | 25.9273 | 3 | 0.29924 | 2.3984 | 72.01%
17 | 2.3309 | 26.3826 | 3 | 0.32297 | 2.3309 | 68.01%
16 | 2.2613 | 26.8655 | 3 | 0.35048 | 2.2613 | 64.01%
15 | 2.1895 | 27.3796 | 4 | 0.3827 | 2.1895 | 60.01%
14 | 2.1153 | 27.9291 | 4 | 0.41473 | 2.1153 | 56.01%
13 | 2.0384 | 28.5193 | 4.5 | 0.45247 | 2.0384 | 52.02%
12 | 1.9585 | 29.1568 | 4.5 | 0.49336 | 1.9585 | 48.02%
11 | 1.8752 | 29.8498 | 4.5 | 0.54233 | 1.8752 | 44.02%
10 | 1.788 | 30.6088 | 5 | 0.60199 | 1.788 | 40.02%
9 | 1.6963 | 31.4477 | 5 | 0.66882 | 1.6963 | 36.02%
8 | 1.5994 | 32.3855 | 5 | 0.75234 | 1.5994 | 32.02%
7 | 1.4962 | 33.4485 | 5 | 0.8597 | 1.4962 | 28.02%
6 | 1.3853 | 34.6755 | 5 | 1.0028 | 1.3853 | 24.02%
5 | 1.2648 | 36.1264 | 5 | 1.203 | 1.2648 | 20.03%
4 | 1.1315 | 37.9016 | 5 | 1.5032 | 1.1315 | 16.03%
3 | 0.98021 | 40.1891 | 5 | 2.003 | 0.98021 | 12.03%
2 | 0.80086 | 43.41 | 5 | 3.0006 | 0.80086 | 8.029%
1 | 0.5674 | 48.9029 | 5 | 5.9778 | 0.5674 | 4.03%
0 | 0.05 | 87.6183 | 5 |  | 0.05 | 0.0313%
All of these values, transfer from Worksheet 1 or C
Uplink channel or sector spectral efficiency at maximum range
Uplink cell spectral efficiency for a specific cell spacing. Assumes 3-sector cell site & takes account reuse factor

## 13-Latency Analysis
13-Analysis to Assess Latency Requirements | There are no entries to be made on this sheet. All relevant parameters are transferred from Sheet C
Denotes values transferred from | Sheet C |  |  | Confidence = binomdist(# of Slots,# of Devices,Prob,Cum)
Limiting Channel Direction is | DL
Path Loss Model | Erceg-SUI-Modified |  | Hata-Okumura |  | Cost231-Hata |  | WINNER II |  | ITU-R M.2135-14
Avgerage Channel Goodput in bps (from Sheet C) = | 2078700 | bps |  | bps |  | bps |  | bps |  | bps
Network Link Latency Required in sec (From Sheet C) = L = | 1.4 | sec | 1.4 | sec | 1.4 | sec | 1.4 | sec | 1.4 | sec
Packet Size (bytes) (From Sheet C) = | 259 | Bytes | 259 | Bytes | 259 | Bytes | 259 | Bytes | 259 | Bytes
Avg Packet Size/DataRate = Avg Time per pkt = TPKT = | 0.00099678 | Sec | #VALUE! | Sec | #VALUE! | Sec | #VALUE! | Sec | #VALUE! | Sec
Probability Message Falls within Latency Window = L/TMSG = | 56.48% |  | 56.48% |  | 56.48% |  | 56.48% |  | 56.48%
Latency/Packet Time = L/PT = # of Slots = | 1404 |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE!
Confidence Level (from Sheet C) = | 99.5% |  | 99.5% |  | 99.5% |  | 99.5% |  | 99.5%
# of Actors or Terminals Supported = | 2351 |  | #N/A |  | #N/A |  | #N/A |  | #N/A
| Confidence | # of Devices | Confidence | # of Devices | Confidence | # of Devices | Confidence | # of Devices | Confidence | # of Devices
| 50.71% | 2486 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 74.59% | 2458.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 90.15% | 2431.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 97.3% | 2404.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 99.49% | 2377.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 99.94% | 2350.75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 99.99% | 2323.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2296.65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2269.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2242.55 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2215.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2188.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2161.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2134.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2107.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2080.25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2053.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 2026.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1999.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1972.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1945 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1917.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1890.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1863.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1836.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1809.75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1782.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1755.65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1728.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1701.55 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1674.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1647.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1620.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1593.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1566.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1539.25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1512.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1485.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1458.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1431.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 100% | 1404 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## 14-Misc-Calculations
This sheet is for illustrative purposes only. It shows the relationship between availability per link and number of series or parallel links
Links in series, as for a Multi-hop or Multi-link Scenario | [5 empty] | Links in parallel, as for a Self-Configuring MESH topology
| Per Link Probability | 99.5% | 99% | 98.5% | 98% | Desired Availability | 99% | 98% | 95% | 93% | 90%
| # of Links or hops | E2E Probability | E2E Probability | E2E Probability | E2E Probability | # of Alternate Paths | Link Availability | Link Availability | Link Availability | Link Availability | Link Availability
| 1 | 99.5% | 99% | 98.5% | 98% | 1 | 99% | 98% | 95% | 93% | 90%
| 2 | 99% | 98.01% | 97.02% | 96.04% | 2 | 90% | 85.86% | 77.64% | 73.54% | 68.38%
| 3 | 98.51% | 97.03% | 95.57% | 94.12% | 3 | 78.46% | 72.86% | 63.16% | 58.79% | 53.58%
| 4 | 98.01% | 96.06% | 94.13% | 92.24% | 4 | 68.38% | 62.39% | 52.71% | 48.56% | 43.77%
| Desired E2E Probability | 99.5% | 99% | 98.5% | 98%
| # of Links or hops | Probability per Link | Probability per Link | Probability per Link | Probability per Link
| 1 | 99.5% | 99% | 98.5% | 98% | Prop of Fade
| 2 | 99.75% | 99.5% | 99.25% | 98.99% | 1 | 1% | 2% | 5% | 7% | 10%
| 3 | 99.83% | 99.67% | 99.5% | 99.33% | 2 | 1% | 2% | 5% | 7% | 10%
| 4 | 99.87% | 99.75% | 99.62% | 99.5% | 3 | 1% | 2% | 5% | 7% | 10%
| 5 | 99.9% | 99.8% | 99.7% | 99.6%
| 6 | 99.92% | 99.83% | 99.75% | 99.66%
| 7 | 99.93% | 99.86% | 99.78% | 99.71%
| 8 | 99.94% | 99.87% | 99.81% | 99.75%
| 9 | 99.94% | 99.89% | 99.83% | 99.78%
| 10 | 99.95% | 99.9% | 99.85% | 99.8%